# Documento candidato completo -- DRAFT

ESTADO: DRAFT. Los cambios documentales NO garantizan por si solos cumplimiento final -- requiere revision QA/Validacion humana (IMPLEMENTATION_VERIFICATION y REGULATORY_COMPLIANCE quedan SIEMPRE fuera de este sistema). El original nunca fue modificado (SOURCE_IMMUTABLE).

Functional Specification (FS)

MCCPDC - SCADA and PCS MISC. PLC System

Customer: Mark Cuban Cost Plus Drug Company, PBC

Project: MCCPDC - SCADA and PCS MISC. PLC System

Project number: 215115305

Document Information

ID code: 215115305-FS Version: 1.2

File: 215115305 SCADA-PCS Misc PLC System FS_v1.2.docx

Archive: <Project Path>\02.10 FS

Rockwell Automation Function: Date: Signature:

Author: Buol, Scott RA-PDM

Review: RA-PQR

Approval: Jason Sampers RA-PM

Mark Cuban

Cost Plus

Drug Function: Date: Signature:

Company,

PBC

Review: C-PM

Review: C-QA

Approval: C-QR

© 2022 Rockwell Automation, Inc. All Rights Reserved Page 1 of 58

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Revision History and Modification List

# Relevant chapter / pages Edited by Target version Date

1 Whole document SAB 1.0 April 15, 2022

Generation of the document

2 SAB 1.1 April 21, 2022

Delete unexpected word “unten” page 23.

Changed screen name from “Alarm History” to “Alarm Details” all occurrences.

3 Updated based on Change TA 1.2 December 16,

Order # 3 2022

Table 1-1 - Revision History and Modification List

Reference Documents

# Document D code / ID code

User Requirement Specifications MCCPDC - SCADA 215115305 SCADA-PCS MISC

[1]

and PCS MISC. PLC System PLC System URS

[2] Control System Architecture diagram 215115305_SYS_ARCH

[3] Water For Injection (WFI) Sequence of Operations 63FFVL02-P-PD-0001

[4] EMS Sequence of Operations 63FFVL02-P-PD-0002

[5] Material and Personnel Flows diagram 63FFVL02-A-A21-100

[6] 21 CFR Part 11 Electronic Records, Electronic 21CFRP11

Signatures

[7] 21 CFR Part 211 Current Good Manufacturing 21CFRP211

Practice for finished Pharmaceuticals

[8] Good Automated Manufacturing Practice, Guide for GAMP5

Validation of Automated Systems 5, ISPE 2008

[9] Control programming specification 215115305 Control

Programming Guideline

[10] HMI programming specification 215115305 HMI Programming

Guideline

[11] MCCPDC PCS-CP01 Alarms Hard Soft IO Listing MCCPDC PCS-CP01 Alarms

Hard Soft IO Listing revB.xls

[12] FactoryTalk View Site Edition User’s Guide VIEWSE-UM006O-EN-E

ID code: 215115305 -FS (V1.2) Page 2 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Reference Documents

# Document D code / ID code

[13] FactoryTalk View Site Edition Installation Guide VIEWSE-IN003R-EN-E

[14] HMI Screen Mock-Ups MCCPDC_HMI_ScreenShots_

Dec20_2022.pdf

Table 1-2 - Reference Documents

ID code: 215115305 -FS (V1.2) Page 3 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Contents

1 Introduction ............................................................................................................................. 7

Purpose ................................................................................................................................ 7

Applicable Regulations, Standards ......................................................................................7

Document Conventions ........................................................................................................7

2 Project Overview .................................................................................................................... 9

Key Objectives and Benefits ................................................................................................9

Project Assumptions, Conventions and Limitations ............................................................. 9

Non-Conformance with User Requirements ......................................................................1 0

Scope ................................................................................................................................. 11

3 Functions and Processes ....................................................................................................1 3

F01.00: Hardware .............................................................................................................. 13

F02.00: System-Level Software Requirements .................................................................1 9

F03.00: Water For Injection (WFI) Sequence of Operations .............................................. 21

F04.00: EMS (Environmental Monitoring System) Sequence of Operations ..................... 21

F05.00: SCADA Process Visualization ..............................................................................2 2

Graphical Screens ............................................................................................................. 25

F06.00: Recipe parameter handling ...................................................................................3 6

F07.00: Alarms, Warning Messages and Error reporting ................................................... 36

F08.00: Reporting .............................................................................................................. 39

4 Security ................................................................................................................................. 40

F09.00: Physical Security ..................................................................................................4 0

F10.00: Logical Security ....................................................................................................4 0

5 Data ........................................................................................................................................ 45

F11.00: Databases and Historical Logging ........................................................................ 45

F12.00: Audit Trail ..............................................................................................................4 5

F13.00: Long-Term Archiving and Data Retrieval ..............................................................4 7

F14.00: Backup and recovery ............................................................................................4 7

F15.00: Frequency of data point collection ........................................................................4 7

6 External Interfaces ............................................................................................................... 49

F16.00: PLC Interfaces (PCS-CP01 and other Vendor Systems) ..................................... 49

ID code: 215115305 -FS (V1.2) Page 4 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F17.00: Non-PLC Interfaces ..............................................................................................5 0

7 Non-Functional Attributes ...................................................................................................5 1

F18.00: System Design ......................................................................................................5 1

F19.00: Availability ............................................................................................................. 51

F20.00: Redundancy ..........................................................................................................5 1

F21.00: Maintainability ....................................................................................................... 52

F23.00: System Performance ............................................................................................5 3

8 Appendix ............................................................................................................................... 54

Glossary, Abbreviations, Acronyms, Definitions ................................................................ 54

Vendor Interface Definition Documentation .......................................................................5 4

List of Functions ................................................................................................................. 54

Traceability URS - Requirements to FS-Functions ............................................................5 5

Figures

No table of figures entries found.

Tables

Table 1-1 - Revision History and Modification List ............................................................................. 2

Table 1-2 - Reference Documents ..................................................................................................... 3

Table 2-1: Software packages to be loaded on system hardware ................................................... 11

Table 2-2: Minimum Server/Client System Requirements Overview ............................................... 12

Table 3-1: Programmable Logic Controller hardware ...................................................................... 16

Table 3-2: HMI Screen List ............................................................................................................... 23

Table 3-3: Overview Screen Display Content .................................................................................. 27

Table 3-4: Environmental Readings Screen Display Content .......................................................... 29

Table 3-5: Filler Vendor Skid Screen Display Content ..................................................................... 29

Table 3-6: Serialization Vendor Skid Screen Display Content ......................................................... 30

Table 3-7: Vial Labeler Vendor Skid Screen Display Content .......................................................... 30

Table 3-8: Parts Washer / Sterilizer Vendor Skid Screen Display Content ...................................... 31

Table 3-9: Parts Washer / Sterilizer Vendor Skid Screen Display Content ...................................... 32

Table 3-10: Waste Lift and Neutralization Vendor Skid Screen Display Content ............................. 33

Table 3-11: Water for Injection (WFI) Vendor Skid Screen Display Content .................................... 34

Table 3-12: Weigh Dispense Vendor Skid Screen Display Content ................................................. 34

Table 3-13: Alarm Limit Modification Screen Display Content ......................................................... 36

Table 3-14: Alarm Categories .......................................................................................................... 38

Table 3-15: Alarm Priorities and Alarm Limit Modification Rules ..................................................... 38

Table 3-16: OEM Supplied External Systems and associated Alarm Type ..................................... 39

Table 4-1: Security levels for this system ......................................................................................... 42

ID code: 215115305 -FS (V1.2) Page 5 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Table 4-2: Security Code Assignments for Graphic Displays ........................................................... 44

Table 5-1: Data point collection frequency by type .......................................................................... 48

Table 8-1: Vendor Interface Specification Documents ..................................................................... 54

ID code: 215115305 -FS (V1.2) Page 6 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

## 1 Introduction

Purpose

This Functional Specification has been produced by MAVERICK Technologies (referred to as “Supplier”)

for Mark Cuban Cost Plus Drug Company, PBC (referred to as “Customer”). It describes the

functionality of the computerized system ‘MCCPDC - SCADA and PCS MISC. PLC System’ along with

any interfaces to demonstrate how the system will meet the requirements specified in the approved User

Requirements Specification (reference documents [1]).

This Functional Specification establishes the basis for the system development and acceptance testing.

Applicable Regulations, Standards

See Table 1-2 - Reference Documents.

Document Conventions

Functions that are described in this document are identified uniquely throughout this document in the

headline of a document section by: “F<Function number>.<Function Item Number>:”

Function Items are used to detail a specific function (group), if necessary.

The ‘Function Number’ starts from 1 and is increased by 1 throughout this document. The ‘Function Item

Number’ starts from 0 for each Function and is increased by 1 for each Function Item.

An important characteristic of a Functional Specification is demonstrating that it meets all of the stated

User Requirements. This document meets and then exceeds that requirement in two ways. First, for a

given Functional Item, the original text with reference number “UR4.1.1 xxx” can be seen at the start of

each requirement. Second, an Index Table found at the end of this document gathers each of the

URx.x.x requirements and lists them beside their satisfying Functional Specification number. This is then

followed by the functional specification page number, allowing direct lookup of a URS by numbered

reference. (See underlined portion below.)

UR4.1.1 [MCCPDC 3.2.3] - The physical servers shall be ... redundant server-F01.01, 10

In this project, the customer has supplied numbered requirements which were retained when the URS

was generated. For traceability, both the URS requirement number and the original customer

requirement number are retained here. As can be seen below, the User Requirement Specification

UR4.1.1 requirement includes in its text, the customer reference number MCCPDC 3.2.3, followed by

the requirement text. (See underlined portion below.)

UR4.1.1 [MCCPDC 3.2.3] - The physical servers shall be…

ID code: 215115305 -FS (V1.2) Page 7 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

In order to maintain unique numbering of approved functions over the document life-time,

 New function groups or function items are appended to the appropriate chapter or section

with an increased function number, and

 Obsolete functions are kept in the document, but the function text is removed by the term

“Obsolete with version <version number>”.

ID code: 215115305 -FS (V1.2) Page 8 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

## 2 Project Overview

Key Objectives and Benefits

The Dallas, TX M3 Fill Finish Line owned by Mark Cuban Cost Plus Drug Company, PBC is a

pharmaceutical production line adhering to FDA requirements.

The new SCADA and PCS Misc. PLC system that will be installed in the M3 Fill Finish Line at Mark

Cuban Cost Plus Drug Company, PBC, performs limited control, collects environmental data, and

collects data from six production machines. The SCADA and PCS Misc. PLC system will interface with

the production machines and their various brands of PLCs.

The SCADA system hardware consists of the following server and clients:

 PCS Physical Servers: located in the Data Room (Room 056, Grid: C1-C2).

 Client 1: Engineering Workstation PC located in Room 054 Grid: A4.

 Client 2: Touchscreen PC used for operator interaction with associated PLC panel for

control located in Utilities Room (Room 035 Grid: B2).

 Client 3 (Group): Wireless Tablet PCs used for operator interaction with the process

located within wireless coverage area on the site.

The supervisory software will be delivered and configured by MAVERICK Technologies. All servers and

clients’ hardware will be installed and connected to the network by Mark Cuban Cost Plus Drug

Company, PBC. The communication between the server and the Ethernet distribution switch in the Data

Room will be established through copper Ethernet cabling and from there, local Ethernet cabling will

connect the different clients and PLC’s. The wireless tablet PCs will connect to the servers in the Data

Room via wireless access points throughout the facility.

Project Assumptions, Conventions and Limitations

This document assumes that the Customer has a basic understanding of, and familiarity with Rockwell

Automation’s FactoryTalk View Site Edition (SE) functionality.

The following limitations and assumptions are known:

1. Per RFI-001, the recipe system requirements do not apply to the SCADA and PCS MISC.

PLC System.

2. In the September 14, 2021 meeting, MCCPDC approved a change from NEMA 4X to

NEMA 12 since the panel is now located in a general use, non-washdown area. UR4.5.2

[URS-PCS-HR-014] Electrical enclosures shall be washdown duty, NEMA 4X rated no

longer applies. The chosen panel with rating of NEMA 4 exceeds the rating requirement

of NEMA 12, thus satisfying the requirement.

ID code: 215115305 -FS (V1.2) Page 9 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Non-Conformance with User Requirements

The proposed system design implements all user requirements except:

Req-ID # Requirement Description Reason

None. N/A.

ID code: 215115305 -FS (V1.2) Page 10 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Scope

Software

The following application software packages and the configuration files will be installed by MAVERICK

Technologies.

Software Version Computer

Windows Server 2016 Standard 16-Core 2016 Server

Win Server 2016 Server Device CAL (5pk) 2016 Server

Win Server 2016 RDS Device CAL (5pk) 2016 Server

Excel Professional 2016 32-bit 2016 32-bit Server

ThinManager V-FLEX 1 Perpetual 12.0.0 Server

FactoryTalk Linx Enterprise 6.21.00 Server

FactoryTalk Alarms and Events 6.21.00 Server

FactoryTalk Activation Manager 4.05.01 Server

FactoryTalk View Studio Site Edition Enterprise

12.0.0 Server

Perpetual

FactoryTalk View Site Edition 10-Client Bundle

12.0.0 Server

Perpetual

FactoryTalk Historian Site Edition – 250 points 7.01 Server

FactoryTalk Historian DataLink Excel Reporting

5.50.02 Server

Tool – Single User

Studio 5000 Logix Designer Standard Perpetual 33.00.00 Server

Cisco Digital Network Architecture Advantage -

3-year Switch

Term License (3 years) – 48 ports

Table 2-1: Software packages to be loaded on system hardware

Hardware

While the hardware for the PCS MISC Control System will be supplied by MAVERICK Technologies, the

installation will be done by others. The server hardware is a VersaVirtual™ Solution comprising

redundant server hardware. The mentioned system software (Table 2-1 above) will be installed by

MAVERICK Technologies.

ID code: 215115305 -FS (V1.2) Page 11 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

The following overview gives the minimum system requirements for the server and clients:

Server/Clients Minimum required hardware Minimum required system software

VMware vCenter Server

10 core CPU VMware vSAN Witness

Server 128 GB RAM VMware PhotonOS based DNS Server (NetSvcs)

2 TB Disk Rockwell Automation Remote Monitoring &

Administration probe (Support)

Intel Atom, x7-E3950, 1.60 GHz

Wired Client 4GB RAM ThinManager® software ready

2 x 1 Gb Ethernet RJ45 LAN ports

Touchscreen, 802.11x Wireless ThinManager® compatible (WinTMC)

Wireless Client

Radio (Windows 10 Operating System)

Table 2-2: Minimum Server/Client System Requirements Overview

ID code: 215115305 -FS (V1.2) Page 12 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

## 3 Functions and Processes

F01.00: Hardware

F01.01: System Server

This function implements the following user requirement(s)

UR4.1.1 [MCCPDC 3.2.3] - The physical servers shall be two (2) redundant Rockwell VersaVirtual™

Appliances suitable for installation in the Data Center racks provided by VDS (Voice-Data-

Security). System provided is one system that has two redundant servers within it.

UR3.5.2 [MCCPDC 1.4.2.4] - The SI shall implement thin client architecture for the SCADA/HMI to allow

process control in a sustainable and scalable platform and to seamlessly integrate skids

PLC’s and OIT’s while providing features, tools, and methods of access which make it

simple to monitor and adjust user sessions.

A Rockwell Automation VersaVirtual™ Appliance is provided. The single system consists of two

redundant servers that provide for a highly available system.

A ThinManager® software solution provides the thin client architecture for the SCADA/HMI as

required.

F01.02: System Ethernet Switch

This function implements the following user requirement(s)

UR4.9.2 [URS-PCS-HR-021] All switching and cabling shall be capable of gigabit data transfer, where

applicable.

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).

A Cisco Catalyst 9300 Network Advantage, 48 port Ethernet switch provides the connectivity

between the VersaVirtual Appliance, the MISC. PLC, and the other networked system components.

The switch is capable of gigabit data transfer.

F01.03: Engineering Workstation

This function implements the following user requirement(s)

UR3.3.5 Hardcopy/electronic data collection requirements

1. All logged data shall be capable of being transferred to external equipment for print our

and/or storage.

UR4.2.1 System shall include a dedicated engineering workstation PC suitable for installation in a

dedicated PC & Print room/office with general purpose area classification.

UR4.2.2 Engineering workstation PC shall include a method to annunciate audible alarms (speakers).

UR4.2.3 System shall include a color duplex printer suitable for installation in a dedicated PC & Print

room/office with general purpose area classification.

ID code: 215115305 -FS (V1.2) Page 13 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

This function implements the following user requirement(s)

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to

the PCS Miscellaneous PLC configuration and shall be capable of being connected to the

OIT’s.

UR3.3.5 Hardcopy/electronic data collection requirements

1. All logged data shall be capable of being transferred to external equipment for print out

and/or storage.

The Engineering Workstation consists of:

one (1) Rockwell ThinManager® Client computer,

one (1) Dell U2719D UltraSharp 27” LED monitor (QHD resolution 2560x1440),

one (1) Dell AE515M speaker/microphone soundbar,

one (1) Dell wireless keyboard,

one (1) Dell wireless mouse, and

one (1) Lexmark C3326dw color duplex laser printer.

This Engineering Workstation will be connected to the ethernet network allowing it to be connected to

the PCS Miscellaneous PLC and the OITs.

The ThinManager® software allows the Engineering workstation to access the Rockwell

Automation’s Studio 5000 Logix Designer programming software to perform online and offline

changes to the PCS Miscellaneous PLC configuration files. (Also discussed in Section 7.1.1.)

The ThinManager® software allows the Engineering workstation to access the Rockwell

Automation’s FactoryTalk View Studio programming software to perform online and offline changes

to the HMI screens and configuration files. (Also discussed in Section 7.1.1.)

The printer connected to the Engineering Workstation meets the requirement for printing.

F01.04: Wireless Tablet PCs

This function implements the following user requirement(s)

UR4.2.4 System shall include three portable Microsoft Surface Pro wireless tablets, each with 12.3”

screen, charger, IP65 stainless steel housing with carrying handle suitable for operation in

GMP cleanrooms.

UR4.4.1 Operator Interface Terminals (OIT’s) shall be provided for the operator to perform process

monitoring and process control.

UR3.5.3 [MCCPDC 2.1.3.2] - The system shall have the ability to wirelessly communicate with tablet PCs

for HMI display and control.

The Wireless Tablet PCs consists of three portable Microsoft Surface Pro wireless tablets, each with

12.3” screen, charger, IP65 stainless steel housing with carrying handle suitable for operation in

GMP cleanrooms.

ID code: 215115305 -FS (V1.2) Page 14 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F01.05: Operator Interface (field mounted)

This function implements the following user requirement(s)

UR4.2.5 System shall include a 15” touchscreen HMI in the face of the PCS Miscellaneous PLC panel.

UR4.4.1 [URS-PCS-HR-006] Operator Interface Terminals (OIT’s) shall be provided for the operator to

perform process monitoring and process control.

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to

the PCS Miscellaneous PLC configuration and shall be capable of being connected to the

OIT’s.

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).

An Industrial Integrated-Display ThinManager Client, Single Core, 15.6 in. Widescreen Display,

Projected Capacitive Multi-Touch Screen, No SSD, Dual Port Ethernet, ThinManager® Ready,

Single Display Output, 24 VDC will provide local touchscreen control of the PCS PLC System.

F01.06: Programmable Logic Controller System (Misc. PLC)

This function implements the following user requirement(s)

UR4.3.1 [URS-PCS-HR-001] The PCS Miscellaneous Programmable Logic Controller (PLC) platform shall

be Rockwell Automation ControlLogix.

UR4.3.2 [URS-PCS-HR-002] The machine control system must have sufficient network connections to

allow for the connection to higher level SCADA systems such as virtual active directory,

network time protocol server, data historian, etc.

UR4.9.1 [URS-PCS-HR-020] Communication between SCADA and plant PLC’s shall be via Ethernet

protocol. All communication cabling shall be CAT6/CAT6A and in compliance with

ANSI/TIA/EIA-568-B standards.

UR4.9.2 [URS-PCS-HR-021] All switching and cabling shall be capable of gigabit data transfer, where

applicable.

UR4.10.1 [URS-PCS-HR-022] The field inputs and outputs to the PCS Miscellaneous PLC shall be

hardwired I/O

1. All analog signals shall be input and output at 4-20 mA.

2. All digital inputs and outputs shall be 24VDC to and from the I&C hardware.

UR4.10.2 [MCCPDC 3.2.2] All stick-build field instrumentation will be powered from the PCS PLC Panel

(2-wire loop-powered and 4-wire instruments).

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).

UR3.6.1 Stick-Build PCS I/O shall be directly wired to the PCS miscellaneous PLC Panel to facilitate

control and GMP monitoring. (reference document- 63FFVL02-J-IO-0001)

UR3.6.2 [MCCPDC 1.4.2.7] - The Environmental Monitoring System (EMS) instruments shall be part of the

project stick-build instrumentation and shall be directly wired to the PCS Miscellaneous PLC

Panel to facilitate GMP monitoring. No independent EMS will exist.

A control system based on Rockwell’s Allen-Bradley ControlLogix Programmable Automation

Control platform is the basis of the automation system (1756- family). This system contains digital

and analog input and output cards to meet the hardwired system I/O requirements. The PLC has

sufficient copper Ethernet communication ports and internal ‘connections’ to communicate via

Ethernet as required. The PLC Ethernet port can communicate at 1 gigabit/sec data transfer rate.

ID code: 215115305 -FS (V1.2) Page 15 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Manufacturer Model Description

Allen-Bradley 1756-PA75 ControlLogix, 85-265 VAC Power Supply (13 Amp @ 5V)

Allen-Bradley 1756-L83E ControlLogix 5580 Controller with 10 MB User Memory, USB

Port, 1 gigabit (Gb) Ethernet port, 250 Ethernet/IP Devices, 4

Character Alpha/Numeric Display.

Allen-Bradley 1756-IF16 Analog Input - Current/Voltage 16 Pts (36 Pin)

Allen-Bradley 1756-OF4 Analog Output - Current/Voltage 4 Pts (20 Pin)

Allen-Bradley 1756-IB16 10-31 VDC Digital Input 16 Pts (20 Pin)

Allen-Bradley 1756-OB16I 10-30 VDC Isolated Digital Output 16 Pts (36 Pin)

Table 3-1: Programmable Logic Controller hardware

F01.07: Access Level Ethernet Switch

This function implements the following user requirement(s)

UR4.3.2 [URS-PCS-HR-002] The machine control system must have sufficient network connections to

allow for the connection to higher level SCADA systems such as virtual active directory,

network time protocol server, data historian, etc.

UR4.4.2 [URS-PCS-HR-007] Ethernet switch shall be provided for communications connectivity between

the PCS Miscellaneous PLC and its OIT, and external systems. Ethernet switch shall be

powered by 24VDC.

UR4.9.1 [URS-PCS-HR-020] Communication between SCADA and plant PLC’s shall be via Ethernet

protocol. All communication cabling shall be CAT6/CAT6A and in compliance with

ANSI/TIA/EIA-568-B standards.

UR4.9.2 [URS-PCS-HR-021] All switching and cabling shall be capable of gigabit data transfer, where

applicable.

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to

the PCS Miscellaneous PLC configuration and shall be capable of being connected to the

OIT’s.

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).

In the PCS MISC. control panel, an access layer Stratix Ethernet switch provides connectivity for the

PLC and the local HMI station. The PLC and HMI communicate via the Ethernet/IP protocol over

CAT6/CAT6A cabling.

PCS MISC. access layer switch for the local PLC and local HMI provides 100Base-T

communications (100 Megabit), not gigabit transfer rates. Gigabit transfer rates are not applicable to

this PLC and this HMI.

ID code: 215115305 -FS (V1.2) Page 16 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F01.08: PCS Miscellaneous PLC Panel and Construction

This function implements the following user requirement(s)

UR4.3.3 [URS-PCS-HR-003] The PCS Miscellaneous PLC Panel shall have no power source greater than

50V except in the dedicated UPS compartment. The PLC panel shall not require Personal

Protection Equipment (PPE) for arc flash during maintenance and calibration. The panel

shall be properly labeled to indicate this condition.

UR4.5.2 [URS-PCS-HR-014] Electrical enclosures shall be washdown duty, NEMA 4X rated.

UR4.5.7 [MCCPDC 7.2.3] The SI shall provide PCS Miscellaneous PLC Panel Heat Load Calculation &

Electrical Loading Calcs. These calculations shall be maintained through to the final

validated state As-Builts.

A Hoffman panel with part number: A74H6018LP3PT describes a steel, NEMA 4, free-standing, two-

door enclosure. This Hoffman enclosure and the MAVERICK partition design allows for the

existence of a “lower voltage area” and a “higher voltage area”. The high voltage area is a separate

compartment that isolates the power source and components which have voltages higher than 50V.

In this way, a user can open the door for the lower voltage area to perform maintenance and

calibration activities and will not be exposed to higher voltages which satisfies this requirement. A

sticker indicating the high voltage side will be affixed to the panel. A sticker indicating the low voltage

side will be affixed to the panel.

In the September 14, 2021 meeting, MCCPDC approved a change from NEMA 4X to NEMA 12

since the panel is now located in a general use, non-washdown area. UR4.5.2 [URS-PCS-HR-014]

Electrical enclosures shall be washdown duty, NEMA 4X rated no longer applies. The chosen panel

with rating of NEMA 4 exceeds the rating requirement of NEMA 12, thus satisfying the requirement.

The heat load calculations were performed, and appropriate ventilation was specified to ensure no

component exceeds its recommended operating window.

F01.09: Uninterruptible Power Supply System (UPS)

This function implements the following user requirement(s)

UR4.3.4 [MCCPDC 3.2.2] The PCS Miscellaneous PLC panel shall have a UPS battery back-up system

installed.

UR4.3.5 [MCCPDC 3.2.2] The PCS Miscellaneous PLC panel UPS shall be capable of supplying the

connected system power for at least fifteen (15) minutes of operation after loss of facility

electrical power.

The selected Hoffman free standing two-door enclosure and the MAVERICK partition design also

allow for the placement of an Uninterruptible Power Supply (UPS) System on the high voltage side.

The Tripp Lite UPS Model: SU2200XLA has been sized appropriately to power the connected

system for the fifteen (15) minute duration as specified.

ID code: 215115305 -FS (V1.2) Page 17 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F01.10: Electrical Components and Craftmanship

This function implements the following user requirement(s)

UR4.5.1 [URS-PCS-HR-013] All wiring inside the machine must be separated into power, signal, and

network channels.

UR4.5.3 [URS-PCS-HR-015] All electrical components shall be UL listed.

UR4.5.5 [MCCPDC 3.2.2] Completed, assembled panel shall be UL certified.

UR4.5.6 [MCCPDC 3.2.2] Completed, assembled panel shall be UL listed for the appropriate electrical

area classification.

Plastic wire ducting within the panel allows for the proper separation of wiring into the three

categories: power, signal, and network cabling.

All electrical components have been selected to carry the UL mark and are UL listed.

The PCS Miscellaneous PLC panel is UL certified as indicated by its certification sticker and

registration with UL.

The PCS Miscellaneous PLC panel has a NEMA 4 rating. It will be placed into Room 035 Utilities

which has a general-purpose classification rating.

F01.11: Electrical Disconnect Switch

This function implements the following user requirement(s)

UR4.5.4 [URS-PCS-HR-016] A lockable disconnect switch shall be provided on each main feed to the

PCS Miscellaneous PLC Panel enclosure. The disconnect switch shall be rated per NEC

guidelines of supplied voltage and current ratings (minimum 600VAC / 30A / Non-Fused).

The Allen-Bradley disconnect switch model 194E-E32-1753-6N is a lockable disconnect switch

which meets this requirement.

F01.12: Stack Light (Color and Function)

This function implements the following user requirement(s)

UR4.6.1 [URS-PCS-HR-017] All indicator lights shall be suitable for operation on 24VDC. Lamps (LED

preferred) and caps shall be replaceable from the outside front of the panel. For lamp caps

specified as colored in hardware design specifications, the lamp cap colors shall be as

follows…Stack light shall be visible from as many operating areas as possible. (see below)

UR4.6.1 [URS-PCS-HR-017] All indicator lights shall be suitable for operation on 24VDC. Lamps (LED

preferred) and caps shall be replaceable from the outside front of the panel. For lamp caps specified as

colored in hardware design specifications, the lamp cap colors shall be as follows (unless otherwise

specified):

1. Red – General meaning is “Not Operating” (e.g., motor not running, device is de-energized, valve is

closed.).

2. Green – General meaning is “Operating” (e.g., motor is running, device is energized, valve is open.).

3. Amber – General meaning is “Warning” or “Take Note” (e.g., subsystem in mode other than normal,

valve is in an intermediate state such as traveling between closed and open.).

Stack light shall be visible from as many operating areas as possible.

ID code: 215115305 -FS (V1.2) Page 18 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

The selected Allen-Bradley 856T family stack light model is three-color light stack which meets this

requirement. The stack light will be mounted on a 10” riser to increase its visibility in the production

area. The three-color assembled stack light consists of a base module and the color light modules:

856T-BMAP25, 856T-BT3, 856T-BT5, 856-BT4, and 856T-B24C.

F01.13: Electrical Component Lifetime

This function implements the following user requirement(s)

UR4.7.1 [URS-PCS-HR-018] All components of the system shall be specified with a mean-time between

failures of more than 2 years.

Where possible, the manufacturer’s documentation, which lists their components’ mean-time

between failure values, is provided.

F01.14: Audible Annunciation

This function implements the following user requirement(s)

UR4.8.1 [URS-PCS-HR-019] System shall have the ability to alert users with an audible alert… (see

below)

UR4.8.1 [URS-PCS-HR-019] Alarm Modules shall:

1. Be panel front mounted, 30mm, fully enclosed with a smooth front or stack light mounted.

2. Have a minimum sound output of 72 dB @ 3 feet.

3. Not de-rate the NEMA rating of the enclosure or shall be stack light mounted

4. No be de-energized from the E-Stop circuit.

The Allen-Bradley sounder module 856T-BP1 is 70mm (larger), stack light mounted, and has an

output of 85 dB (louder) to alert users in the area of an alarm condition. The mounting shall be made

such that the NEMA rating of the enclosure is not de-rated. As the E-Stop requirement for this

system has been removed per RFI-001, the audible alarm is not dependent on the E-Stop circuit.

F02.00: System-Level Software Requirements

F02.01: General Software Requirements

This function implements the following user requirement(s)

UR3.2.5 System must implement electronic signatures.

UR5.2.1 [URS-PCS-SR-007] The system shall be configured to host an operator interface application.

UR5.3.1 [URS-PCS-SR-030] The control system programming shall use Control Modules and standard

programming per ISA S88/S95 as applicable.

ID code: 215115305 -FS (V1.2) Page 19 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

This function implements the following user requirement(s)

UR5.3.2 [URS-PCS-SR-031] Operations shall contain steps (series of actions) and transitions (conditions

required for sequence to progress) to perform required process sequences.

UR5.4.1 [URS-PCS-SR-035] The system shall provide for an interface for the collection and archival of

continuous process data, alarms, alarm acknowledgement, events, parameters, and

ancillary data.

UR5.4.4 [URS-PCS-SR-038] The system must provide tools to automatically adjust for daylight and

standard time changes without loss of data or operation.

UR5.4.7 [URS-PCS-SR-041] The PLC system shall communicate with a plant historian (collect and

transfer data).

UR3.5.1 Language requirements for operator and non-operator dialogs boxes (administrators).

Information will be displayed in English.

The Rockwell Software Factory Talk View SE platform shall be configured to make use of electronic

signature features.

The delivered system has the Rockwell Software FactoryTalk View SE software loaded onto it, which

hosts an operator interface application. The delivered system has a custom operator interface

application written for monitoring and, where appropriate, controlling the connected systems.

The control system is programmed using control modules and follows the S88/S95 standards as

applicable.

Process sequences have been programmed with steps and transitions as required, based on

descriptions in the control logic narratives.

The Rockwell Software FactoryTalk View SE platform provides the ability to archive continuous

process data, alarms, alarm acknowledgement, events, parameters, and ancillary data.

The alarm and events service saves all alarms and events in Universal Coordinated Time (UTC)

without any time zone offsets or daylight savings adjustments added. When the events are retrieved

from the database for viewing, local time zone offsets or daylight savings adjustments can be applied.

In this way, the system does not lose any accuracy or data due to daylight savings or time zone

offsets.

The FactoryTalk Historian system reads data from the PCS-CP01 PLC and logs it appropriately.

The operator interface text will be displayed in English.

F02.02: Modes of Operation

This function implements the following user requirement(s)

UR3.2.1 Mode of operations- Ready for WFI Sampling, WFI Sampling, Sanitization, WFI valves implement

Automatic and Manual Modes.

The WFI system for the Mark Cuban Cost Plus Drug Company, PBC facility consists of a WFI

Generation Skid, Tank, Distribution Skid, and Loop with manual automated valves. The automated

ID code: 215115305 -FS (V1.2) Page 20 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

valves serve the parts washer / sterilizer and clean steam generator. The loop components

controlled by the PCS system, their required actions, sequences and modes are described in the

Water For Injection (WFI) Sequence of Operations document (reference documents [3]).

F02.03: Input Simulation

This function implements the following user requirement(s)

UR5.3.3 [URS-PCS-SR-032] All inputs shall provide state and simulation features. This shall be captured

on a separate maintenance screen, accessible by Admin and Maintenance personnel.

Simulation logic exists for each input to allow an HMI user to force the state of the input to a desired

value regardless of the state of the wired input signal (actual input).

F02.04: Historian Unavailability Check

This function implements the following user requirement(s)

UR5.4.9 [URS-PCS-SR-043] A secured level access manual override shall be required / available to start

a new batch without active heartbeat connection to the plant historian.

Batches and batch logic do not apply to the PCS Misc. PLC system and its functions.

F03.00: Water For Injection (WFI) Sequence of Operations

As mentioned above, the WFI system for the Mark Cuban Cost Plus Drug Company, PBC

facility consists of a WFI Generation Skid, Tank, Distribution Skid, and Loop with manual and

automated valves. The automated valves serve the parts washer / sterilizer and clean steam

generator. The loop components controlled by the PCS system and their required actions are

described in the Water For Injection (WFI) Sequence of Operations document (reference documents

[3]).

F04.00: EMS (Environmental Monitoring System) Sequence of Operations

The Environmental Monitoring System Sequence of Operations is described in the EMS

Sequence of Operations document (reference documents [4]).

ID code: 215115305 -FS (V1.2) Page 21 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F05.00: SCADA Process Visualization

The FactoryTalk View SE HMI enables operators and production personnel to view and monitor the

process. Visualization of the process is established through different screens that show the important

process data and critical process parameters.

This function implements the following user requirement(s)

UR5.2.9 [URS-PCS-SR-015] The system shall provide display of analog signal status, numerical values,

engineering units, and alarming.

UR5.2.18 [URS-PCS-SR-024] All soft key buttons shall be of sufficient size to allow finger touch of the

object to activate it and have adequate space between objects to ensure the correct object

is being selected. Soft key button sizing and locations shall be approved during design

review. The OIT shall provide a mechanism to confirm operator actions (e.g., pop-up

window, etc.).

The FactoryTalk View SE HMI satisfies the requirements for a method to display the values

described as well as a method to generate pop-up windows. Guidelines for colors, font sizes,

graphics to use, and more are discussed in the HMI programming specification (reference document

[10]).

HMI Screen List

Number Screen Name Screen File Name Description

Overview screen displaying critical

1 Overview Overview

parameters

Environmental Environmental readings for each of the

2 Monitoring System EnvironReadings areas (temperature, relative humidity,

(EMS) Pressure), Compressed Air Readings

3 Trends Trends Data point trending display

Digital Input Point Status of digital input points and simulation

4 InputPointStatDig

Statuses and Simulation interface

Analog Input Point Status of analog digital input points and

5 InputPointStatAna

Statuses and Simulation simulation interface

6 Alarm Details AlarmDetails Displays current and historical alarm details

Ability to modify alarm limits from OIT

7 Alarm Limit Modification AlarmLimitModification

(page 1 of 2)

Ability to modify alarm limits from OIT

8 Alarm Limit Modification AlarmLimitModification2

(page 2 of 2)

9 Filler Filler Filler vendor skid points

Vial Labeler / Vial Labeler vendor skid points and

10 VialLabelerSerial

Serialization Serialization vendor skid point

11 Parts Washer / Sterilizer PartsWasherSterilizer Parts Washer / Sterilizer vendor skid points

ID code: 215115305 -FS (V1.2) Page 22 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Screen Name Screen File Name Description

Waste Lift and Waste Lift and Neutralization vendor skid

12 WasteNeutralLift

Neutralization Station points

13 Water for Injection WaterForInjection Water For Injection vendor skid points

14 Clean Steam Generator CleanSteam Clean Steam Generator vendor skid points

15 Weigh / Dispense WeighDispense Weigh / Dispense vendor skid points

Table 3-2: HMI Screen List

F05.01: Trending

This function implements the following user requirement(s)

UR5.2.19 [URS-PCS-SR-025] Real-time multi-pen trends for all analog and defined discrete signals. Also,

PID loop controller screens to include trending for PV, SP and CV as applicable.

The system provides the ability to trend any of the tags in the PCS-CP01 PLC controller which

includes both analog and discrete signals. Tags can be added and removed at runtime. The

trending requirement for the PV, SP, and CV of the PID loops does not apply since there are no PID

loops under the control of the PCS-CP01 system.

F05.02: Display colors of dynamic objects

This function implements the following user requirement(s)

UR5.2.20 [URS-PCS-SR-026] The following colors shall be utilized when indicating states of dynamic

objects…(see below)

The following colors shall be utilized when indicating states of dynamic objects:

1. Gray – General meaning is “Not Operating” (e.g., motor not running, device is de-

energized, valve is closed).

2. Green – General meaning is “Operating” (e.g., motor is running, device is energized,

valve is open.).

3. Yellow – General meaning is “Warning” or “Take Note” (e.g., device is in a mode

other than normal such as manual mode, valve is in an intermediate state such as

manual mode, valve is in an intermediate state such as traveling between closed and

open).

4. Red – General meaning is “Alarm” or “Lockout” (e.g., an alarm is active on a device or

Operation, lockout is activated).

The color palette is applied to dynamic objects to reflect the colors shown above.

ID code: 215115305 -FS (V1.2) Page 23 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F05.03: Print Screen Function

This function implements the following user requirement(s)

UR5.2.21 [URS-PCS-SR-027] The capability to generate an electronic or hard copy of any active display

must be available via the Print Screen function.

A Print Screen button visible on each display allows for the capture of that display for later review.

F05.04: Overview Screen

This function implements the following user requirement(s)

UR5.2.23 [URS-PCS-SR-029] The system shall provide an “Overview” screen on all physical OITs. The

overview screen will display “view-only” data for all critical parameters, values and

information across the system. Details of the required overview information to be determined

during detailed design.

An Overview Screen (Main) is provided which displays the critical parameters, values, and

information as described in Section 3.1.12 Overview Screen below.

F05.05: Input State and Simulation Review Screen

This function implements the following user requirement(s)

UR5.3.3 [URS-PCS-SR-032] All inputs shall provide state and simulation features. This shall be captured

on a separate maintenance screen, accessible by Admin and Maintenance personnel.

An Input State and Simulation Review screens are present which are only accessible to the

Administrator and Maintenance login security levels. These screens displays the state of the wired

input (actual input) and the state of the simulated input and if the simulation function is active for that

particular input (simulated state is what controller sees).

Since an Administrator or Maintenance person may put any input point in SIMULATE and change its

value, it is the responsibility of this person to supervise and adjust the manually inserted value for any

points placed in SIMULATE. Failure to properly supervise and adjust manually inserted values may

cause incorrect control functions and may lead to equipment damage.

F05.06: PLC firmware version and OIT version available via HMI

This function implements the following user requirement(s)

UR5.2.17 [USR-PCS-SR-023] The PLC revision will be addressed to a PLC register, and hard coded OIT

revision shall be accessible via a main menu selection to users with Administrator or

Engineer security level privileges.

ID code: 215115305 -FS (V1.2) Page 24 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

The PLC application revision is populated into a tag in the PCS-CP01 PLC. The OIT software

application revision is populated into a tag in the PCS-CP01 PLC. Both of these tags are visible via

the main menu selection to any user in the Administrator or Maintenance Engineer security level

groups. (Engineer security level group is not a valid group on this system).

F05.07: Display Access and Navigation

All the HMI screens in this project are contained within a FactoryTalk View SE project which exists on

the FactoryTalk View SE server. As such, all screens will be available to all clients both wired and

wireless, which have access to the server, depending on their security access level.

Graphical Screens

A menu bar available near the top of each screen provides the ability to navigate to the screens in the list

below. These are available on every screen but for readability of this document, they are not listed in

each screen’s object list.

 Overview

 Input Point Statuses and Simulation

 Environmental Readings

 Waste Lift and Neutralization

 Water for Injection (WFI)

 Weigh / Dispense

 Parts Washer / Sterilizer

 Filling System

 Vial Labeler / Serialization

 Clean Steam Generator

 Trends

An Alarm Banner near the top of each screen displays alarms and a button is provided which displays

the Alarm Details screen. This is available on every screen but for readability of this document, it is not

listed in each screen’s object list.

 Alarm Details

Per the specification a Print Screen button is available on each screen to capture the current screen

contents. This is available on every screen but for readability of this document, it is not listed in each

screen’s object list.

 Print Screen Button

ID code: 215115305 -FS (V1.2) Page 25 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Overview Screen

The project start-up screen is the Overview screen, which gives an overview of the critical process

parameters and navigation options to each of the sub-screens including the vendor screens.

From the Overview screen, one also has the ability to perform the following actions:

 Login

 Logout

 Change password

 Print Screen

 Shutdown PanelView (exit to configure mode)

At minimum, this screen displays the following items:

Number Information to Description

display

1 XI-00001-04, 05, 06 PCS Overall Status Indicator

2 XAH-00001-06 PCS Overall Status (Horn) Indicator

3 XS-30001-8 BMS Common Trouble Input Signal Indicator

4 AAHH-33002-02, 03 Filler VHP Hi-Hi Alarm Horn Indicator

5 ALH-33002-02, 03 Filler VHP High Alarm Strobe Indicator

6 XI-99001-24A, B EMS Status Light (Alarm/Normal) Corridor 24 Indicator

7 XI-99001-37A, B EMS Status Light (Alarm/Normal) Corridor 37 Indicator

8 Software signal Water For Injection System Common Trouble Indicator

Parts Washer Sterilizer / Clean Steam Generator Common

9 Software signal

Trouble Alarm indicator

XA-33002-04

10 Filler System Common Trouble Alarm Indicator

Software signal

11 Software signal Vial labeler Common Trouble Indicator

UI 36210-01

12 Serialization Common Trouble Indicator

Software signal

13 Software signal Waste Lift / Neutralization Station Common Trouble Indicator

14 XI-00001-01 PCS Common Trouble Output Signal to BMS Indicator

15 XI-00001-02 EMS Common Trouble Output Signal to BMS Indicator

Compressed Air Supply to Filters Dew Point numeric display

16 AIT-08001-02

deg F (Td)

ID code: 215115305 -FS (V1.2) Page 26 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

Compressed Air Supply to Filters Hydrocarbons numeric

17 AIT-08001-03

display mg/m^3

18 PIT-08001-08 Compressed Air Header Pressure numeric display PSI

36 Software signal Weigh / Dispense System Common Trouble Indicator

Cold Room Storage System Common Trouble Indicator

37 Software signal

(pending processing of Cold Room Storage change request)

38 Software signal OIT software version (from PLC register) per specification

39 Software signal PLC firmware version (from PLC register) per specification

40 - Login button

41 - Logout button

42 - Change Password button

43 - Print Screen button

44 - Shutdown button

Table 3-3: Overview Screen Display Content

Environmental Readings

At minimum this screen displays the following items:

Number Information to Description

display

1 HIT-99001-05 Relative Humidity - Rm. 005

2 PDIT-99001-05 Differential Pressure - Rm. 005

3 TIT-99001-05 Temperature - Rm. 005

4 PDIT-99001-07 Differential Pressure - Rm. 007

5 HIT-99001-09 Relative Humidity - Rm. 009

6 PDIT-99001-09 Differential Pressure - Rm. 009

7 TIT-99001-09 Temperature - Rm. 009

8 PDIT-99001-28 Differential Pressure - Rm. 028

9 PDIT-99001-29 Differential Pressure - Rm. 029

10 PDIT-99001-30 Differential Pressure - Rm. 030

11 PDIT-99001-31 Differential Pressure - Rm. 031

ID code: 215115305 -FS (V1.2) Page 27 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

12 HIT-99001-33 Relative Humidity - Rm. 033

13 PDIT-99001-33 Differential Pressure - Rm. 033

14 TIT-99001-33 Temperature - Rm. 033

15 HIT-99001-34 Relative Humidity - Rm. 034

16 PDIT-99001-34 Differential Pressure - Rm. 034

17 TIT-99001-34 Temperature - Rm. 034

18 PDIT-99001-37 Differential Pressure - Corr. 037

19 PDIT-99001-37A Differential Pressure - Corr. 037

20 HIT-99001-39 Relative Humidity - Rm. 039

21 PDIT-99001-39 Differential Pressure - Rm. 039

22 TIT-99001-39 Temperature - Rm. 039

23 PDIT-99001-40 Differential Pressure - Rm. 040

24 PDIT-99001-40A Differential Pressure - Rm. 040(2)

25 PDIT-99001-41 Differential Pressure - Rm. 041

26 PDIT-99001-43 Differential Pressure - Rm. 043

27 Software signal Cold Room Storage Humidity (pending change request)

28 Software signal Cold Room Storage Temperature (pending change request)

29 HIT-99001-46 Relative Humidity Cage Storage - Rm. 046

30 TIT-99001-46 Temperature Cage Storage - Rm. 046

31 TIT-99001-50A Temperature Transmitter - COLUMN B5 - HIGH

32 HIT-99001-50A Humidity Transmitter - COLUMN B5 - HIGH

33 TIT-99001-50B Temperature Transmitter - COLUMN B5 – LOW

34 HIT-99001-50B Humidity Transmitter - COLUMN B5 – LOW

35 TIT-99001-50C Temperature Transmitter - COLUMN B6 – HIGH

37 HIT-99001-50C Humidity Transmitter - COLUMN B6 - HIGH

38 TIT-99001-50D Temperature Transmitter - COLUMN B6 – LOW

39 HIT-99001-50D Humidity Transmitter - COLUMN B6 – LOW

40 TIT-99001-50E Temperature Transmitter - COLUMN C6 – HIGH

41 HIT-99001-50E Humidity Transmitter - COLUMN C6 - HIGH

42 TIT-99001-50F Temperature Transmitter - COLUMN C6 – LOW

43 HIT-99001-50F Humidity Transmitter - COLUMN C6 - LOW

ID code: 215115305 -FS (V1.2) Page 28 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Table 3-4: Environmental Readings Screen Display Content

Trends

Trending screen allowing user selection of the pen(s) of interest to be displayed.

Input Point Statuses and Simulation Screen

Each of the digital and analog input points will be displayed with the ability to simulate the input per the

specification (See 3.1.9, F05.05: Input State and Simulation Review Screen).

Filler Vendor Skid Screen

Filler screen includes a basic block diagram of process and, at minimum, includes the signals listed in

the table below.

Number Information to Description

display

1 AAHH-33002-02, 03 Filler VHP Hi-Hi Alarm Horn Indicator

2 ALH-33002-02, 03 Filler VHP High Alarm Strobe Indicator

3 Software signal Filler Run Status

XA-33002-04

4 Filler System Common Trouble Alarm Indicator

Software signal

XA-33002-05

5 Particulate Count High Level

Software signal

Filler Room (Rm. 034) Vaporous Hydrogen Peroxide

6 AIT-33002-01

Concentration

DP-33002

7 Peristaltic Pump Run Status

Software signal

Table 3-5: Filler Vendor Skid Screen Display Content

ID code: 215115305 -FS (V1.2) Page 29 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Serialization Vendor Skid Screen

There are no static graphics to display for the Serialization Vendor Skid. At minimum, the

signals listed in the table below are included.

Number Information to Description

display

1 Software signal Serialization Run Status

UI-36210-01

2 Serialization Common Trouble Indicator

Software signal

Table 3-6: Serialization Vendor Skid Screen Display Content

Vial Syringe Labeler Vendor Skid Screen

There are no static graphics to display for the Vial Labeler Vendor Skid. At minimum, the signals

listed in the table below are included.

Number Information to Description

display

1 Software signal Vial Labeler Run Status

2 Software signal Vial Labeler Common Trouble Indicator

Table 3-7: Vial Labeler Vendor Skid Screen Display Content

Parts Washer / Sterilizer Vendor Skid Screen

Parts Washer / Sterilizer screen includes a basic block diagram of process and, at minimum, includes

the signals listed in the table below. Since this device has communications for control purposes,

additional handshaking logic with the Parts Washer / Sterilizer PLC is required.

Number Information to Description

display

1 Software signal Parts Washer / Sterilizer (Clean Steam Generator) Run Status

XA-32001-04 Parts Washer / Sterilizer (Clean Steam Generator) Common

2

Software signal Trouble Alarm Indicator

XA-11001-02

3 WFI System ready to dispense (Available)

Software signal

ID code: 215115305 -FS (V1.2) Page 30 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

XS-32001-06 Parts Washer / Sterilizer is requesting Water For Injection

4

Software signal (WFI)

Parts Washer / Sterilizer (Clean Steam Generator)

5 Software signal

Communication OK (heartbeat logic based on rolling register)

6 HY-32001-03 WFI Block Valve Solenoid at POU command state

7 HY-32001-02 WFI Block Valve Solenoid – Sampling command state

Washer / Sterilizer POU Valve Closed limit switch status (this is

8 ZSC-32001-03

shown implicitly via the valve open/close state)

Washer / Sterilizer POU Valve Open limit switch status (this is

9 ZSO-32001-03

shown implicitly via the valve open/close state)

Washer / Sterilizer Sample Point Valve Closed limit switch

10 ZSC-32001-02

status (this is shown implicitly via the valve open/close state)

Washer / Sterilizer Sample Point Valve Open limit switch status

11 ZSC-32001-02

(this is shown implicitly via the valve open/close state)

Table 3-8: Parts Washer / Sterilizer Vendor Skid Screen Display Content

Clean Steam Generator Vendor Skid Screen

Clean Steam Generator screen includes a basic block diagram of process and, at minimum, includes the

signals listed in the table below. Since this device has communications for control purposes, additional

handshaking logic with the Parts Washer / Sterilizer (Clean Steam Generator) PLC is required.

Number Information to Description

display

1 Software signal Parts Washer / Sterilizer (Clean Steam Generator) Run Status

XA-32001-04 Parts Washer / Sterilizer (Clean Steam Generator) Common

2

Software signal Trouble Alarm Indicator

XA-11001-02

3 WFI System ready to dispense (Available)

Software signal

Clean Steam Generator is requesting Water For Injection

4 Software signal

(WFI)

Parts Washer / Sterilizer (Clean Steam Generator)

5 Software signal

Communication OK (heartbeat logic based on rolling register)

6 HY-32002-03 WFI Block Valve Solenoid at POU command state

ID code: 215115305 -FS (V1.2) Page 31 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

7 HY-32002-02 WFI Block Valve Solenoid - Sampling command state

Clean Steam POU Valve Closed limit switch status (this is

8 ZSC-32002-03

shown implicitly via the valve open/close state)

Clean Steam POU Valve Open limit switch status (this is

9 ZSO-32002-03

shown implicitly via the valve open/close state)

Clean Steam Sample Point Valve Closed limit switch status

10 ZSC-32002-02

(this is shown implicitly via the valve open/close state)

Clean Steam Sample Point Valve Open limit switch status (this

11 ZSC-32002-02

is shown implicitly via the valve open/close state)

Table 3-9: Parts Washer / Sterilizer Vendor Skid Screen Display Content

Waste Lift and Neutralization Vendor Skid Screen

Waste Lift and Neutralization screen includes a basic block diagram of process and, at minimum,

includes the signals listed in the table below.

Number Information to Description

display

1 Software signal Waste Lift and Neutralization Run Status

2 Software signal Waste Lift and Neutralization Common Trouble Indicator

PU-23005

3 Acid Pump Run Status

Software signal

PU-23006

4 Base Pump Run Status

Software signal

PU-23002

5 Drain Pump Run Status

Software signal

PU-23001-01

6 Waste Equalization Tank Waste Pump 1

Software signal

PU-23001-02

7 Waste Equalization Tank Waste Pump 2

Software signal

LSHH-23001-01

8 Waste Equalization Tank High-High Level

Software signal

ID code: 215115305 -FS (V1.2) Page 32 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

LSH-23001-01

9 Waste Equalization Tank High Level

Software signal

LSL-23001-01

10 Waste Equalization Tank Low Level

Software signal

LSLL-23001-01

11 Waste Equalization Tank Low-Low Level

Software signal

FI-23001-01

12 Discharge Flow

Software signal

Table 3-10: Waste Lift and Neutralization Vendor Skid Screen Display Content

Water for Injection (WFI) Vendor Skid Screen

Waste Lift and Neutralization screen includes a basic block diagram of process and, at minimum,

includes the signals listed in the table below. Since this device has communications for control

purposes, additional handshaking logic with the WFI PLC is required.

Number Information to Description

display

1 YI-12004-01 WFI Ready Indicator - Rm. 007

2 YI-12004-03 WFI Ready Indicator - Rm. 023

3 YI-12004-02 WFI Ready Indicator - Rm. 009

4 YI-31010-03 WFI Ready Indicator - Rm. 033

XA-11001-02

5 WFI System ready to dispense (Available)

Software signal

XA-11001-03

6 WFI System Common Trouble Indicator

Software signal

XS-32001-06 Parts Washer / Sterilizer is requesting Water For Injection

7

Software signal (WFI)

Clean Steam Generator is requesting Water For Injection

8 Software signal

(WFI)

9 Software signal WFI System is actively sanitizing the system

WFI Communication OK (heartbeat logic based on rolling

10 Software signal

register)

ID code: 215115305 -FS (V1.2) Page 33 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

11 AIT-11001-01 Reverse Osmosis Discharge Conductivity

12 AIT-11001-02 Reverse Osmosis Header Conductivity

13 FIT-11101-04 Reverse Osmosis Header Flow

14 LIT-12002-13 WFI Storage Tank Level

15 TIT-12002-14 WFI Storage Tank Temperature

16 HS-12002-01 WFI Storage Fill Valve

17 QIT-845.6.1 WFI Distrubution Return TOC (Total Organic Compounds)

18 QIT-845.8.1 WFI Distribution Return Conductivity

19 TIC-845.8.1 WFI Distribution Return Temperature

Table 3-11: Water for Injection (WFI) Vendor Skid Screen Display Content

Weigh Dispense Vendor Skid Screen

Weigh Dispense screen includes a basic block diagram of process and, at minimum, includes the

signals listed in the table below.

Number Information to Description

display

XA-30001-8

1 Weigh Dispense Common Trouble Indicator

Hardwired signal

Table 3-12: Weigh Dispense Vendor Skid Screen Display Content

Alarm Details Screen

Alarm Details screen includes an Alarm object which displays all of the current and historical alarms.

Alarm Limit Modification Screens

Each of the points will be displayed including its upper and lower alarm limit with the ability to change the

alarm limit value. Spans multiple screens with the same title to accommodate the needed points. At

minimum, this screen displays the following values:

ID code: 215115305 -FS (V1.2) Page 34 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

1 AIT-08001-02 Compressed Air Supply to Filters

2 AIT-08001-03 Compressed Air Supply to Filters

3 PIT-08001-08 Compressed Air Header

4 HIT-99001-05 Relative Humidity - Rm. 005

5 PDIT-99001-05 Differential Pressure - Rm. 005

6 TIT-99001-05 Temperature - Rm. 005

7 PDIT-99001-07 Differential Pressure - Rm. 007

8 HIT-99001-09 Relative Humidity - Rm. 009

9 PDIT-99001-09 Differential Pressure - Rm. 009

10 TIT-99001-09 Temperature - Rm. 009

11 PDIT-99001-28 Differential Pressure - Rm. 028

12 PDIT-99001-29 Differential Pressure - Rm. 029

13 PDIT-99001-30 Differential Pressure - Rm. 030

14 PDIT-99001-31 Differential Pressure - Rm. 031

15 HIT-99001-33 Relative Humidity - Rm. 033

16 PDIT-99001-33 Differential Pressure - Rm. 033

17 TIT-99001-33 Temperature - Rm. 033

18 HIT-99001-34 Relative Humidity - Rm. 034

19 PDIT-99001-34 Differential Pressure - Rm. 034

20 TIT-99001-34 Temperature - Rm. 034

21 PDIT-99001-37 Differential Pressure - Corr. 037

22 PDIT-99001-37A Differential Pressure - Corr. 037

23 HIT-99001-39 Relative Humidity - Rm. 039

24 PDIT-99001-39 Differential Pressure - Rm. 039

25 TIT-99001-39 Temperature - Rm. 039

26 PDIT-99001-40 Differential Pressure - Rm. 040

27 PDIT-99001-40A Differential Pressure - Rm. 040

28 PDIT-99001-41 Differential Pressure - Rm. 041

29 PDIT-99001-43 Differential Pressure - Rm. 043

30 AIT-33002-01 Vaprous Hydrogen Peroxide (VHP)

31 HIT-99001-46 Relative Humidity Cage Storage - Rm. 046

ID code: 215115305 -FS (V1.2) Page 35 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Number Information to Description

display

32 TIT-99001-46 Temperature Cage Storage - Rm. 046

33 TIT-99001-50A Temperature Transmitter - COLUMN B5 - HIGH

34 HIT-99001-50A Humidity Transmitter - COLUMN B5 - HIGH

35 TIT-99001-50B Temperature Transmitter - COLUMN B5 – LOW

36 HIT-99001-50B Humidity Transmitter - COLUMN B5 – LOW

37 TIT-99001-50C Temperature Transmitter - COLUMN B6 – HIGH

38 HIT-99001-50C Humidity Transmitter - COLUMN B6 - HIGH

39 TIT-99001-50D Temperature Transmitter - COLUMN B6 – LOW

40 HIT-99001-50D Humidity Transmitter - COLUMN B6 – LOW

41 TIT-99001-50E Temperature Transmitter - COLUMN C6 – HIGH

42 HIT-99001-50E Humidity Transmitter - COLUMN C6 - HIGH

43 TIT-99001-50F Temperature Transmitter - COLUMN C6 – LOW

44 HIT-99001-50F Humidity Transmitter - COLUMN C6 - LOW

45 Software signal Cold Room Storage Humidity (pending change request)

46 Software signal Cold Room Storage Temperature (pending change request)

Table 3-13: Alarm Limit Modification Screen Display Content

F06.00: Recipe parameter handling

Per RFI-001, the recipe system requirements do not apply to the SCADA and PCS MISC. PLC System.

F07.00: Alarms, Warning Messages and Error reporting

This function implements the following user requirement(s)

UR5.1.2 [URS-PCS-SR-002] Distinction shall be drawn between, process interlocks, and safety interlocks

lock out conditions.

UR5.2.7 [URS-PCS-SR-013] Interlock shall have associated alarms.

UR5.2.8 [URS-PCS-SR-014] Bypassed interlock conditions shall be clearly indicated at the OIT.

UR5.2.9 [URS-PCS-SR-015] The system shall provide display of analog signal status, numerical values,

engineering units, and alarming.

UR5.2.10 [URS-PCS-SR-016] Alarm presentation shall be visual and audible.

UR5.2.11 [URS-PCS-SR-017] Alarms shall be displayed at the OIT as they occur. An alarm summary shall

be available as a navigable screen at the OIT.

UR5.2.12 [URS-PCS-SR-018] Each alarm should have its own description that is traceable for

troubleshooting by a line operator or maintenance person.

ID code: 215115305 -FS (V1.2) Page 36 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

This function implements the following user requirement(s)

UR5.2.13 [URS-PCS-SR-019] Alarm acknowledgement and silencing of audible alarms shall be done from

the OIT.

UR5.2.16 [URS-PCS-SR-022] The system must detect and inform the operator of failures or errors in

hardware and non-responsive equipment.

UR5.2.22 [URS-PCS-SR-028] Alarms shall be stored / available to view on an alarm history screen.

F07.01: List of Alarms

This function implements the following user requirement(s)

UR3.2.3 The Equipment shall have critical alarms and warnings as listed in (URS) Table 1- List of Critical-

to-Quality Alarms.

1. The list of critical alarms in the (URS) table is not intended to be a comprehensive list of

all alarms for the system. A complete alarm list is included in the Functional Specification

document.

The complete alarm list for this system is found in the document described below.

Document Type Specification Document

Alarm List MCCPDC PCS-CP01 Alarms Hard Soft IO Listing

(reference document [11])

F07.02: Logging of Alarms, Warning Messages and Errors

Logging of Alarms, Warning Messages and Errors is done in a database table of the centralized

database.

Interlocks are conditions which, when active, will cause the effected device to go to its fail-safe state.

The device will not be able to be activated until the interlock condition clears or the device is placed in

Manual mode to override the interlocks. All interlocks shall have associated alarms.

Safety interlocks may not be overridden in any mode.

Process interlocks may be overridden with appropriate access level.

Trip conditions shall be locked out for safety.

A screen named Alarm Details is available to view past alarms.

F07.03: Alarm Categories

This function implements the following user requirement(s)

UR5.2.14 [URS-PCS-SR-020] Alarms shall be in one of the following categories- Unacknowledged (active

or inactive), Acknowledged (active), and Acknowledged (cleared).

As alarms become active, they shall transition through the following states.

ID code: 215115305 -FS (V1.2) Page 37 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Alarm Category Description

Unacknowledged - Active

 Alarm flashes black text on red background on the alarm banner and

the alarm summary screen.

Unacknowledged - Inactive

 Alarm is displayed in steady black text on red background on the

Acknowledged - Active

alarm banner and the alarm summary screen.

 Alarm is not displayed on the alarm banner and alarm summary

Acknowledged - Cleared

screen.

Table 3-14: Alarm Categories

F07.04: Alarm Priorities and Alarm Limit Modification Rules

This function implements the following user requirement(s)

UR5.3.4 [URS-PCS-SR-033] Alarms shall be classified into three priority categories unless alternative is

approved by MCCPDC. Level 1, Level 2, and Level 3 as described below.

UR5.3.5 [URS-PCS-SR-034] Alarm functionality is to include the ability to change alarm limit values via

user input from the OIT display. This functionality shall be secured level access for level 1

and level 2 alarms only. Changes shall only be capable from Administrator level access.

See the alarm listing to view which alarms have been assigned to which priority level. (Reference:

3.1.26 F07.01: List of Alarms)

The ability to modify the alarm limit values via user input at the OIT is restricted to Priority Level 1 & 2

alarms and only by the Administrator security level.

Alarm Priority Description

 Level 1 alarms serve as warning alarms and will be annunciated on

the OIT’s.

Level 1

 Alarm limit values can be changed via OIT by Administrator security

level.

 Level 2 alarms will serve as operator action alarms and will be

annunciated on the OIT’s and external indicator.

Level 2

 Alarm limit values can be changed via OIT by Administrator security

level.

 Level 3 alarms shall be reserved for interlock or lockout actions and

conditions causing sequences to immediately be deactivated and will

Level 3 be annunciated on the OIT’s and external indicator.

 Alarm limit values cannot be changed by user input.

Table 3-15: Alarm Priorities and Alarm Limit Modification Rules

ID code: 215115305 -FS (V1.2) Page 38 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F07.05: External Interface Alarming

This function implements the following user requirement(s)

UR5.4.5 [URS-PCS-SR-039] The system shall monitor and alarm the status of all dependent external

interfaces.

An alarm message is programmed for each of the connections made to external data sources listed

in Table 3-16. The alarm will become active when the system is disconnected and will reset when

the system is connected.

OEM Supplied External System Alarm Type

WFI Generation, Storage, and Distribution system Connection / Disconnection

Filler System Connection / Disconnection

Vial/Syringe Labeler Connection / Disconnection

Waste Lift and Neutralization System Connection / Disconnection

Washer/Sterilizer with Clean Steam Generator Connection / Disconnection

Sterilization Connection / Disconnection

Table 3-16: OEM Supplied External Systems and associated Alarm Type

F07.06: Historian Availability Alarming

This function implements the following user requirement(s)

UR5.4.8 [URS-PCS-SR-042] The control system shall have a historian heartbeat alarm to monitor the

health of control system communication with the process historian. In absence of an active

connection, this heartbeat alarm will be triggered, however the PLC’s will continue operating.

PCS MISC PLC logic will check for the status of an output tag from the FactoryTalk Historian Server.

The alarm will become active when the process historian data link is disconnected and will reset

when the process historian system is connected.

F08.00: Reporting

F08.01: End of Batch Report

The PCS MISC. PLC System is a monitoring and utility system and does not participate in batch

operations. End of Batch reporting is not implemented for this system.

ID code: 215115305 -FS (V1.2) Page 39 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F08.02: Recipe Printout

Per RFI-001, the recipe system requirements do not apply to the SCADA and PCS MISC. PLC System.

## 4 Security

F09.00: Physical Security

It is essential to limit operator access to the hardware running Windows operating systems and

FactoryTalk View SE. In general, an operator’s only access to the computer should be via the

keyboard, mouse, or touch screen. An operator with access to the power switch and bootable media

could have direct access to the underlying file system and could potentially circumvent many of the

security measures described in this document. It is the responsibility of the Mark Cuban Cost Plus

Drug Company, PBC. to put measures in place to limit operator access and to protect the hardware

systems.

F10.00: Logical Security

This function implements the following user requirement(s)

UR3.4.1 The system shall implement the security and access control requirements of 21 CFR Part 11

requirements for computerized systems, as they are for this system

1. [MCCPDC 3.3.5] – Activity data, including username, will be stored in an event log.

2. HMI to be configured to require operator username and password for login per 21 CFR

Part 11.

UR5.2.2 [URS-PCS-SR-008] Control and privilege access shall be assigned to system users based on the

following operator access levels- Default User, Operator, Supervisor, Maintenance,

Administrator.

UR5.2.6 [URS-PCS-SR-012] The system must have an automatic logout function that after a certain

period of inactivity the user is logged out to Default User.

F10.01: System Security Configuration

Security is used to restrict a user’s access to certain parts of the system. FactoryTalk View SE uses a

combination of Microsoft Windows domain security and FactoryTalk View SE security. While Windows

security is used to authenticate users and restrict operating system level actions, FactoryTalk View SE

runtime security restricts graphical user interface access and control system function access. The

FactoryTalk View SE security is based on a system of letter codes (A-P) which are assigned to the

individual users to define their access.

FactoryTalk View SE makes efficient use of the security features built into the underlying Microsoft

Windows operating systems. For compliance, all FactoryTalk View SE computers in a closed system

must be part of the same Windows domain. Microsoft’s Windows 2019, 2016, 2012, and 10 encrypt

passwords using the operating system’s built-in encryption mechanisms. The FactoryTalk View SE

ID code: 215115305 -FS (V1.2) Page 40 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

server in this system uses Windows Server 2016 while the Engineering Workstation uses Remote

Desktop Client and will be viewing Windows Server 2016 desktops. (see 2.1.1 Software).

Before you can add users and user groups to the accounts list in the FactoryTalk View SE Runtime

Security editor, you have to create accounts for them in FactoryTalk Security services. Add only a subset

of the Microsoft Windows users to FactoryTalk View SE, as needed.

The Windows-linked All Users group is automatically added to the FactoryTalk Runtime Security

accounts. By default, this gives all users access to all FactoryTalk View SE runtime security codes (A-

P), and all FactoryTalk Security actions.

F10.02: FactoryTalk View SE Security

 Use a password-protected screen saver. To ensure that only operators with the proper

credentials are accessing workstations in a closed system, a password-protected screen

saver can be used on the FactoryTalk View SE Client terminals. This system will take the

recommended exception to this rule when critical process data must be displayed at all

times. In this case, a ‘view only’ user account will be logged in to display the status of

production and alarm information.

 Use the included DeskLock software feature to restrict operators’ access to the client’s

operating system.

 Disable switch to other applications since this opens access to other programs.

 Disable ‘Allow display code debugging’ since this allows launching of the VBA editor,

which is not secure.

 Change the window properties of the FactoryTalk View SE Client to disable the title

bar, the system menu, the close button, and the show diagnostics list. Set the window to

be maximized.

F10.03: Configure FactoryTalk View SE clients automatically login as DEFAULT user

after a period of inactivity

Since the system requires that critical operations information be displayed at all times, the DEFAULT

User (a user with ‘view only’ access) shall be logged in when a period of inactivity occurs. This

allows the read-only display of production and alarm information.

FactoryTalk View SE clients can be configured to automatically log out after a specified

period of time, however this feature does not subsequently permit the immediate and automatic login

of another user (DEFAULT) as required. To achieve the required actions, idle conditions will be

detected and then the DEFAULT user will be logged in effectively logging out the current user.

ID code: 215115305 -FS (V1.2) Page 41 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F10.04: Security/Access Levels

The access and manipulation of this system is protected through the FactoryTalk Security software

module which integrates with FactoryTalk View SE. FactoryTalk Security software provides access

based on the system user level. The following security levels are identified for this SCADA project:

Security level Allowed access/action level Security Code

Assignment

DEFAULT User  View/Read only access to graphics with DEFAULT user access A

 All privileges of the DEFAULT User

 Ability to acknowledge alarms

Operator A, B

 Ability to interact with standard equipment control buttons

 Ability to select and activate recipes (N/A for this system)

Supervisor  All privileges of Operator A, B, C

 All privileges of Operator

Maintenance  Ability to view PLC and OIT revision A, B, C, D

 Ability to change input values via simulation feature

 All privileges

 Ability to view PLC and OIT revision

Administrator  Ability to change input values via simulation feature A, B, C, D, E

 Ability to modify alarm limits (Level 1 and Level 2 alarms)

 Ability add, modify, delete recipes (N/A for this system)

Table 4-1: Security levels for this system

User account controls are in compliance with:

UR5.3.3 [URS-PCS-SR-032] All inputs shall provide state and simulation features. This shall be

captured on a separate maintenance screen, accessible by Admin and Maintenance personnel.

UR5.2.17 [USR-PCS-SR-023] The PLC revision will be addressed to a PLC register, and hard

coded OIT revision shall be accessible via a main menu selection to users with Administrator or

Engineer (Maintenance) security level privileges.

UR5.3.5 [URS-PCS-SR-034] Alarm functionality is to include the ability to change alarm limit

values via user input from the OIT display. This functionality shall be secured level access for level

1 and level 2 alarms only. Changes shall only be capable from Administrator level access.

F10.05: User account configuration

This function implements the following user requirement(s)

UR5.2.4 [URS-PCS-SR-010] The user identification must consist of two parts, username and password.

ID code: 215115305 -FS (V1.2) Page 42 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

This function implements the following user requirement(s)

UR5.2.5 [URS-PCS-SR-011] System must be capable of utilizing active directory. It must be possible to

configure the required password strength of the user’s password with items such as # of

capital letters, # of special characters, and length of the password itself.

Both Microsoft Windows domain security and the FactoryTalk System Administration tool can enable the

creation of a unique login and password for each user.

FactoryTalk View SE can use Microsoft Windows security to manage user accounts. Password

expiration, password aging, password complexity requirements, account expiration, disabling of

accounts, lockout after n invalid login attempts, and forcing a change of password on first login are all

security features provided by both Microsoft Windows security and FactoryTalk Security.

Procedures should be implemented to ensure that user IDs do not get deleted or reassigned. It is

recommended to disable user IDs rather than deleting them as a best practice.

The customer’s management procedure should include the verification of the identity of an individual

before sanctioning an individual’s electronic signature.

Once a user has been sanctioned and a unique account with password has been created in the

FactoryTalk View SE system, the user is required to enter his/ her login and password to access

FactoryTalk View SE. This process validates the identity of the user to FactoryTalk View SE.

FactoryTalk View SE requires two components for user identification: a unique login ID and password.

When using the FactoryTalk View SE electronic signature feature, both the user login ID and password

are required to perform an action. The FactoryTalk View SE electronic signature feature can be

configured to display and record the meaning of the signature. It also allows for separate performer and

approval signatures, and for comments to be added regarding the meaning of the signature.

If the user logs out of FactoryTalk View SE and again requires access, the user must reenter the login ID

and password.

F10.06: Security Code Assignments for Graphic Displays

Table 4-2: Security Code Assignments for Graphic Displays defines the security codes assigned to each

graphic display. Referencing Table 4-1, one can determine the user access to each of the screens by

group name.

Graphic Filename Security Code (A-P)1

0F

Overview *, D

Environmental Readings B

Trends B

Input Point Statuses and Simulation2 B, D

1F

1 The Security Code “ * ” indicates all codes (A to P inclusive) are assigned.

1 The Security Code “ * ” indicates all codes (A to P inclusive) are assigned.

ID code: 215115305 -FS (V1.2) Page 43 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Graphic Filename Security Code (A-P)1

0F

Filler B

Serialization B

Vial Syringe Labeler B

Parts Washer / Sterilizer B

Clean Steam Generator B

Waste Lift and Neutralization B

Water for Injection B

Weigh / Dispense B

Alarm Details B

Alarm Limit Modification (page 1 of 2) E

Alarm Limit Modification2 (page 2 of 2) E

3Table 4-2: Security Code Assignments for Graphic Displays

2 Screen access is defined by the first code (least restrictive), additional codes indicate objects on screen are

subject to additional restrictions

ID code: 215115305 -FS (V1.2) Page 44 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Agregar al FS una seccion especifica de politica de retencion de datos historizados, procedimiento de backup y prueba periodica de restauracion, y descripcion explicita de proteccion contra perdida/alteracion de datos (Annex 11 S7.1, S7.2) -- ver COR-5. Verificable mediante revision QA de la nueva seccion mas evidencia de al menos un ciclo de backup/restauracion documentado.

Incluir detalles sobre la sincronización de registros con eventos operativos.

## 5 Data

F11.00: Databases and Historical Logging

This function implements the following user requirement(s)

UR3.3.6 Data retention time on the system

1. The system shall have provision for retaining 1 year of historical data locally before it is

archived in an alternate location for safe keeping.

UR5.4.7 [URS-PCS-SR-041] The PLC system shall communicate with a plant historian (collect and

transfer data).

F11.01: Process Historian

This system contains the Rockwell FactoryTalk Historian SE software and server which

satisfies the requirement to collect and transfer data.

F11.02: Critical Data Records

This system maintains the following critical runtime data records:

 FactoryTalk View SE alarm log and activity log data are stored in the corresponding

databases as analog, digital and string values.

 Analog, digital and string device tags that are transferred from the PLC to the

FactoryTalk View SE system.

F12.00: Audit Trail

This function implements the following user requirement(s)

UR3.3.1 Every time a critical alarm threshold is modified and audit trail record shall be generated. The

record shall contain the following fields

1. Date and time stamps of the change

2. Original threshold value

3. Threshold value after change

4. User ID of the individual who has changed the threshold value (performer)

5. Full name of the individual who has changed the threshold value (performer)

6. Meaning of signature (performer)

7. User ID of the individual who has approved the change (approver)

8. Full name of the individual who has approved the change (approver)

9. Meaning of signature (approver).

UR3.3.2 Every time a critical alarm condition occurs an audit trail record shall be generated with the

following fields

1. Alarm date and time stamps

2. Alarm tag

3. Alarm value

4. Alarm description

5. A similar record shall be generated whenever a critical alarm condition returns to normal

condition.

ID code: 215115305 -FS (V1.2) Page 45 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

This function implements the following user requirement(s)

UR3.3.3 Audit trail records shall be archived.

UR3.3.3 Audit trail records shall be archived.

UR5.2.3 [URS-PCS-SR-009] Logins, logouts, and login attempts must be recorded in the Audit Trail.

UR5.4.2 [URS-PCS-SR-036] All manual interactions (parameter changes, device mode changes, etc.)

shall be sent to a database for event logging, including user name, action and timestamp.

FactoryTalk View SE provides an electronic signature feature for capturing operator actions

performed in the production system. This feature is available in an E-Signature control, as well

as the native button, numeric, and string input objects.

With the FactoryTalk View SE electronic signature feature, each entry into the FactoryTalk View

SE activity log is identified with:

 time and date the action occurred,

 name of the logged-in operator who performed the action,

 terminal the action was performed from,

 type of operation that was performed, and

 value of the changed item before and after the change.

When electronic signatures are used, the operator’s username and full name are also included.

The Critical Alarm Threshold Change Audit Trail entry will contain the following information:

 Date and time stamps of the change

 Original threshold value

 Threshold value after change

 User ID of the individual who has changed the threshold value (performer)

 Full name of the individual who has changed the threshold value (performer)

 Meaning of signature (performer)

 User ID of the individual who has approved the change (approver)

 Full name of the individual who has approved the change (approver)

 Meaning of signature (approver).

The Critical Alarm Audit Trail entry will contain the following information:

 Alarm date and time stamps

 Alarm tag

 Alarm value

 Alarm description

 A similar record shall be generated whenever a critical alarm condition returns to

normal condition.

ID code: 215115305 -FS (V1.2) Page 46 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F13.00: Long-Term Archiving and Data Retrieval

This function implements the following user requirement(s)

UR3.3.7 Data archiving requirements and data storage media.

1. MCCPDC will be responsible for archiving historical data per their internal procedures at

a location of their choosing. Regular archiving is recommended.

MCCPDC will be responsible for long-term archiving of historical data per their internal procedures at

a location of their choosing. Regular archiving is recommended.

F14.00: Backup and recovery

This function implements the following user requirement(s)

UR3.2.2 Failure/Recovery

PLC/HMI

The system shall have the means to recover from a hardware fault by means of

reconfiguration and/or replacement and then reconfiguration.

A list of hardware settings for each device shall be maintained as applicable.

A list of software settings or suitable configuration file(s) for each device shall be maintained

as applicable.

Process Automation Control Server System

The System shall have a means to recover from software corruption or loss of configuration

information by reprogramming or reloading of the appropriate parameters. (Restore from

backup)

A back-up of the PLC program shall be maintained to allow for the restoration of the PLC in the

event it is needed.

A list of hardware settings for the SCADA and PCS Misc. PLC System components shall be

maintained for the restoration of hardware devices.

A list of software settings or suitable configuration file(s) for each device shall be maintained for

the restoration of software-related settings on devices.

A back-up of the FactoryTalk View SE application shall be maintained to allow for the

restoration of the user application in the event it is needed.

F15.00: Frequency of data point collection

This function implements the following user requirement(s)

UR3.2.4 Capacity and speed of data acquisition from MCCPDC

1. The system shall be capable of acquiring a data sample consisting of a combination of at

least 100 data points of analog and/or digital every 15 seconds.

UR3.3.4 Frequency of data point collection

1. The system shall be configurable allowing for differing logging rates depending on signal

type. A table indicating the measurement type and the logging frequency required can be

found in the Functional Specification. (e.g., Temperature sampled every 60 sec.).

This FactoryTalk Historian SE license permits up to 250 points to be logged based on a configurable

rate. One hundred points once every 15 seconds can be accommodated.

This FactoryTalk Historian SE is capable of logging data at different rates based on its configuration.

ID code: 215115305 -FS (V1.2) Page 47 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

The data shall be logged according to rates show in Table 5-1 below.

Data Point Type Frequency of Logging Comment

Relativity Humidity 60 seconds

Pressure (compressed air system) 15 seconds

Differential Pressure (Room) 60 seconds

Dew Point 60 seconds

Hydrocarbons 60 seconds

Pump Speed (RPM) (soft I/O) 5 seconds

Surge Bag Weight (soft I/O) 15 seconds

Vaporous Hydrogen Peroxide

15 seconds

Concentration (VHP)

Type not listed above 60 seconds

Table 5-1: Data point collection frequency by type

The customer representative has recently informed us of their interest in changing their requirement

from time-based to event-based logging. Once agreed upon and formalized, the response to that

change will be reflected here as required.

ID code: 215115305 -FS (V1.2) Page 48 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

## 6 External Interfaces

F16.00: PLC Interfaces (PCS-CP01 and other Vendor Systems)

This function implements the following user requirement(s)

UR3.1.1 The system shall measure the critical process parameters for the process, which include flow,

humidity, dew point, pressure, and temperature.

UR3.5.2 [MCCPDC 1.4.2.4] - The SI shall implement thin client architecture for the SCADA/HMI to allow

process control in a sustainable and scalable platform and to seamlessly integrate skids

PLC’s and OIT’s while providing features, tools, and methods of access which make it

simple to monitor and adjust user sessions.

UR3.6.3 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named

WFI Generation, Storage, and Distribution system. The OEM vendor on-skid control system

platform is Allen-Bradley CompactLogix with 1769 Remote I/O.

UR3.6.4 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named

Filler System. The OEM vendor on-skid control system platform is Allen-Bradley

GuardLogix (1756-L72S).

UR3.6.5 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named

Vial/Syringe Labeler. The OEM vendor on-skid control system platform is Allen-Bradley

CompactLogix (5380 series).

UR3.6.6 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named

Waste Lift and Neutralization System. The OEM vendor on-skid control system platform is

Allen-Bradley MicroLogix or CompactLogix.

UR3.6.7 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named

Washer/Sterilizer with Clean Steam Generator. The OEM vendor on-skid control system

platform is Fedegari THEMA4 & Siemens S7-1512 PLC, with NanoBox IPC227E, and

NanoPanel IPC277E HMI.

UR3.6.8 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named

Serialization. The OEM vendor on-skid control system platform is Beckhoff IPC (Windows

10 with Bosch Rexroth HMI).

This system is comprised of both a local PLC panel (PCS-CP01), which has instruments wired to it, and

vendor systems which also record process parameters. All of these systems will report their data to a

FactoryTalk View SE system with Historian. The connection to all of these systems is what is described

here.

The Rockwell Automation FactoryTalk Linx Enterprise software provides the connection between the

FactoryTalk View SE system and the PLCs (PCS-CP01 and the other vendor systems). This standard

OPC server for Rockwell Controllers provides the means to read/write values from/to the controller. The

relevant OPC tags are listed in the corresponding Vendor Interface Document as shown in Section 8

Appendix, Table 8-1: Vendor Interface Specification Documents.

Rockwell Automation/MAVERICK is aware of additional vendor systems which are expected to be

added to the requirements list and this specification will be updated to include those as required.

ID code: 215115305 -FS (V1.2) Page 49 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

F17.00: Non-PLC Interfaces

This function implements the following user requirement(s)

UR5.4.6 [URS-PCS-SR-040] The system shall communicate via OPC standard communication protocol for

data transfer outside of the PLC control system layer.

The Rockwell Automation FactoryTalk Linx Enterprise software is an OPC server and provides the

connections to non-PLC systems.

ID code: 215115305 -FS (V1.2) Page 50 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

## 7 Non-Functional Attributes

This function implements the following user requirement(s)

UR6.1.1 [MCCPDC 3.3.3] - The project shall utilize the GAMP methodology when developing the system

and documentation.

UR6.1.2 System is documented via entries found in URS Table 2- List of Documents.

F18.00: System Design

This system and its documentation are designed according to the GAMP methodology.

F19.00: Availability

This function implements the following user requirement(s)

UR3.2.2 Failure/Recovery

PLC/HMI

The system shall have the means to recover from a hardware fault by means of

reconfiguration and/or replacement and then reconfiguration.

A list of hardware settings for each device shall be maintained as applicable.

A list of software settings or suitable configuration file(s) for each device shall be maintained

as applicable.

Process Automation Control Server System

The System shall have a means to recover from software corruption or loss of configuration

information by reprogramming or reloading of the appropriate parameters. (Restore from

backup)

PLC/HMI

The PLC and HMI Systems store their programs onboard and, if configured to do so, recover

from power failures and begin running again without the need for user intervention.

Recovery from software corruption is implemented via offline storage of the PLC and HMI

software programs that is re-loaded to the devices should they become corrupted. This is a

restore from backup solution.

Process Automation Control Server System

The Process Automation Control Server System requires user action to start up the system

after a shutdown. Refer to the Rockwell Automation VersaVirtual™ Appliance User Manual

(Publication GMSN-UM001_-EN-P) for instructions on the Start-Up procedure.

F20.00: Redundancy

The PLC logic program and the HMI program shall be stored in discrete memory devices which

can be isolated (either physically or electronically) from the rest of the system to provide offline

redundancy.

ID code: 215115305 -FS (V1.2) Page 51 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Redundant PCS MISC PLC hardware is not present. Should a significant enough failure occur to

the PCS MISC PLC, the PLC will stop functioning and cease to control the process.

For visualization, this system consists of one individual HMI terminal, three wireless tablets, and an

HMI server hosting the display content.

The individual HMI terminal mounted in the PCS CP01 cabinet does not have redundant

hardware. Should a significant enough failure occur to this HMI terminal, the HMI will stop

functioning and not provide a working user interface.

While there are three wireless tablets, which provides a means of redundancy due to multiple

units, the individual tablets do not contain any redundant hardware. Should one fail, the second or

third unit would provide redundancy.

The FactoryTalk View SE HMI server and other software is running on the VersaVirtual™

redundant hardware appliance and should one portion of the underlying hardware fail, the software

will switch to the redundant hardware piece and continue providing service (screens and

connectivity).

As already mentioned, the VersaVirtual™ appliance has hardware redundancy built-in allowing a

failure to occur and not interrupt the functions of the system (FactoryTalk View SE, Historian,

FactoryTalk Security, etc.)

F21.00: Maintainability

F21.01: Programming Software

This function implements the following user requirement(s)

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to

the PCS Miscellaneous PLC configuration and shall be capable of being connected to the

OIT’s.

Per Section 3.1.3 F01.03: Engineering Workstation, an Engineering Workstation is included which

satisfies this requirement.

Per 3.1.7 F01.07: Access Level Ethernet Switch the Ethernet switch is described which will allow

connectivity from the Engineering workstation to the Programmable Logic Controller (PLC) satisfying

the connectivity requirement.

Per Section 2.1.1 Software, Rockwell Automation’s Studio 5000 Logix Designer software is available

which is the Integrated Development Environment software permitting changes to all functions and

features of the Programmable Logic Controller (PLC). As noted in Section 3.1.3 this software is

accessible to the Engineering Workstation via the ThinManager® technology.

Per Section 2.1.1 Software, Rockwell Automation’s FactoryTalk View Studio programming software

is available which is the Integrated Development Environment software permitting changes to all

functions and features of the HMIs. As noted in Section 3.1.3 this software is accessible to the

Engineering Workstation via the ThinManager® technology.

ID code: 215115305 -FS (V1.2) Page 52 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Per Section 2.1.1 Software, Rockwell Automation’s FactoryTalk Historian SE Administration Console

is bundled with the FactoryTalk Historian Site Edition product. The Administration Console is the

programming and configuration software permitting changes to all functions and features of the

FactoryTalk Historian software. As noted in Section 3.1.3 this software is accessible to the

Engineering Workstation via the ThinManager® technology.

F21.02: Application Code/Software

This function implements the following user requirement(s)

UR5.1.3 [URS-PCS-SR-005] All software source code shall be commented by the SI to convey intent and

function of the code.

Each of the subroutines contain a header description as to their function.

Tag names / variable names are named using descriptive text indicating their function and, if needed,

include additional commenting and description.

F22.00: Application Code/Software Revision Control

This function implements the following user requirement(s)

UR5.1.4 [URS-PCS-SR-006] Revision history needed from initiation of SFAT, all revisions shall be

approved and tracked.

Using MAVERICK’s Program Revision Control form, the program changes are logged and accounted for

starting from the time of Software FAT until delivery of the software to the customer.

F23.00: System Performance

There are no specific requirements by Mark Cuban Cost Plus Drug Company, PBC for System

Performance.

F23.01: Operating System Compatibility

This function implements the following user requirement(s)

UR5.2.15 [URS-PCS-SR-021] The system must be compatible with Windows 10 on laptop/desktop clients

and/or Windows Terminal Services.

Per Section 2.1.1 Software, Microsoft Windows Server 2016 is running on the servers and the tablet

PCs will be running Windows 10. The Microsoft Windows Server 2016 product is considered

compatible with Windows 10 with regards to network interoperability and general user interface.

ID code: 215115305 -FS (V1.2) Page 53 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

## 8 Appendix

Glossary, Abbreviations, Acronyms, Definitions

This section includes definitions of terms which may be unfamiliar to the reader or terminology which

have meanings specific to this document or application.

Name Description

FS Functional Specification

DS Design Specification

SCADA Supervisory Control and Data Acquisition

Stick-build Building piece by piece on the job site rather than pre-fabricated which is completely built at the

factory and delivered as a unit.

URS User Requirement Specification

Vendor Interface Definition Documentation

The interface with the various vendor systems listed previously in Section 6 External Interfaces, titled

F16.00: PLC Interfaces (PCS-CP01 and other Vendor Systems) are described in detail in Systems the

following documents.

Vendor System Name Vendor Interface Specification Document

WFI Generation, Storage, and Distribution system

Filler System

Vial/Syringe Labeler

MCCPDC PCS Interface Control Block Narrative

Waste Lift and Neutralization System

Washer/Sterilizer with Clean Steam Generator

Serialization

Table 8-1: Vendor Interface Specification Documents

List of Functions

F01.00: Hardware

F02.00: System-Level Software Requirements

F05.00: SCADA Process Visualization

F07.00: Alarms, Warning Messages and Error reporting

F10.00: Logical Security

F11.00: Databases and Historical Logging

F12.00: Audit Trail

F13.00: Long-Term Archiving and Data Retrieval

F14.00: Backup and recovery

F15.00: Frequency of data point collection

F16.00: PLC Interfaces (PCS-CP01 and other Vendor Systems)

F17.00: Non-PLC Interfaces

F19.00: Availability

F21.00: Maintainability

F23.00: System Performance

ID code: 215115305 -FS (V1.2) Page 54 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

Traceability URS - Requirements to FS-Functions

None.-* N/A *, 10

UR3.1.1 The system shall measure the critical process parameters for the process, which include flow, humidity, dew point, pressure,

and temperature.-F16.00, 49

UR3.2.1 Mode of operations- Ready for WFI Sampling, WFI Sampling, Sanitization.-F02.02, 20

UR3.2.2 Failure/Recovery-F14.00, 47

UR3.2.2 Failure/Recovery-F19.00, 51

UR3.2.3 The Equipment shall have critical alarms and warnings as listed in (URS) Table 1- List of Critical-to-Quality Alarms.-

F07.01, 37

UR3.2.4 Capacity and speed of data acquisition from MCCPDC-F15.00, 47

UR3.2.5 System must implement electronic signatures.-F02.01, 19

UR3.3.1 Every time a critical alarm threshold is modified and audit trail record shall be generated. The record shall contain the

following fields-F12.00, 45

UR3.3.2 Every time a critical alarm condition occurs an audit trail record shall be generated with the following fields-F12.00, 45

UR3.3.3 Audit trail records shall be archived.-F12.00, 46

UR3.3.4 Frequency of data point collection-F15.00, 47

UR3.3.5 Hardcopy/electronic data collection requirements-F01.03, 13, 14

UR3.3.6 Data retention time on the system-F11.00, 45

UR3.3.7 Data archiving requirements and data storage media.-F13.00, 47

UR3.4.1 The system shall implement the security and access control requirements of 21 CFR Part 11 requirements for computerized

systems, as they are for this system-F10.00, 40

UR3.5.1 Language requirements for operator and non-operator dialogs boxes (administrators). Information will be displayed in

English.-F02.01, 20

UR3.5.2 [MCCPDC 1.4.2.4] - The SI shall implement thin client architecture for the SCADA/HMI to allow process control in a

sustainable and scalable platform and to seamlessly integrate skids PLC’s and OIT’s while providing features, tools, and methods

of a-F01.01, 13, 49

UR3.5.3 [MCCPDC 2.1.3.2] - The system shall have the ability to wirelessly communicate with tablet PCs for HMI display and

control.-F01.04, 14

UR3.6.1 Stick-Build PCS I/O shall be directly wired to the PCS miscellaneous PLC Panel to facilitate control and GMP monitoring.

(reference document- 63FFVL02-J-IO-0001)-F01.06, 15

UR3.6.2 [MCCPDC 1.4.2.7] - The Environmental Monitoring System (EMS) instruments shall be part of the project stick-build

instrumentation and shall be directly wired to the PCS Miscellaneous PLC Panel to facilitate GMP monitoring. No independent

EMS will e-F01.06, 15

UR3.6.3 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named WFI Generation, Storage,

and Distribution system. The OEM vendor on-skid control system platform is Allen-Bradley CompactLogix with 1769 Remote

I/O.-F16.00, 49

UR3.6.4 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named Filler System. The OEM

vendor on-skid control system platform is Allen-Bradley GuardLogix (1756-L72S).-F16.00, 49

UR3.6.5 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named Vial/Syringe Labeler. The

OEM vendor on-skid control system platform is Allen-Bradley CompactLogix (5380 series).-F16.00, 49

UR3.6.6 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named Waste Lift and

Neutralization System. The OEM vendor on-skid control system platform is Allen-Bradley MicroLogix or CompactLogix.-

F16.00, 49

UR3.6.7 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named Washer/Sterilizer with Clean

Steam Generator. The OEM vendor on-skid control system platform is Fedegari THEMA4 & Siemens S7-1512 PLC, with

NanoBox IPC227E, an-F16.00, 49

UR3.6.8 [MCCPDC 3.3.1] - The system shall interface with an OEM vendor supplied equipment named Serialization. The OEM

vendor on-skid control system platform is Beckhoff IPC (Windows 10 with Bosch Rexroth HMI).-F16.00, 49

UR4.1.1 [MCCPDC 3.2.3] - The physical servers shall be two (2) redundant Rockwell VersaVirtual™ Appliances suitable for

installation in the Data Center racks provided by VDS (Voice-Data-Security). System provided is one system that has two

redundant server-F01.01, 13

UR4.10.1 [URS-PCS-HR-022] The field inputs and outputs to the PCS Miscellaneous PLC shall be hardwired I/O-F01.06, 15

ID code: 215115305 -FS (V1.2) Page 55 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

UR4.10.2 [MCCPDC 3.2.2] All stick-build field instrumentation will be powered from the PCS PLC Panel (2-wire loop-powered and

4-wire instruments).-F01.06, 15

UR4.2.1 System shall include a dedicated engineering workstation PC suitable for installation in a dedicated PC & Print room/office

with general purpose area classification.-F01.03, 13

UR4.2.2 Engineering workstation PC shall include a method to annunciate audible alarms (speakers).-F01.03, 13

UR4.2.3 System shall include a color duplex printer suitable for installation in a dedicated PC & Print room/office with general

purpose area classification.-F01.03, 13

UR4.2.4 System shall include three portable Microsoft Surface Pro wireless tablets, each with 12.3” screen, charger, IP65 stainless

steel housing with carrying handle suitable for operation in GMP cleanrooms.-F01.04, 14

UR4.2.5 System shall include a 15” touchscreen HMI in the face of the PCS Miscellaneous PLC panel.-F01.05, 15

UR4.3.1 [URS-PCS-HR-001] The PCS Miscellaneous Programmable Logic Controller (PLC) platform shall be Rockwell Automation

ControlLogix.-F01.06, 15

UR4.3.2 [URS-PCS-HR-002] The machine control system must have sufficient network connections to allow for the connection to

higher level SCADA systems such as virtual active directory, network time protocol server, data historian, etc.-F01.06, 15

UR4.3.2 [URS-PCS-HR-002] The machine control system must have sufficient network connections to allow for the connection to

higher level SCADA systems such as virtual active directory, network time protocol server, data historian, etc.-F01.07, 16

UR4.3.3 [URS-PCS-HR-003] The PCS Miscellaneous PLC Panel shall have no power source greater than 50V except in the

dedicated UPS compartment. The PLC panel shall not require Personal Protection Equipment (PPE) for arc flash during

maintenance and calibrati-F01.08, 17

UR4.3.4 [MCCPDC 3.2.2] The PCS Miscellaneous PLC panel shall have a UPS battery back-up system installed.-F01.09, 17

UR4.3.5 [MCCPDC 3.2.2] The PCS Miscellaneous PLC panel UPS shall be capable of supplying the connected system power for at

least fifteen (15) minutes of operation after loss of facility electrical power.-F01.09, 17

UR4.4.1 [URS-PCS-HR-006] Operator Interface Terminals (OIT’s) shall be provided for the operator to perform process monitoring

and process control.-F01.05, 15

UR4.4.1 Operator Interface Terminals (OIT’s) shall be provided for the operator to perform process monitoring and process control.-

F01.04, 14

UR4.4.2 [URS-PCS-HR-007] Ethernet switch shall be provided for communications connectivity between the PCS Miscellaneous

PLC and its OIT, and external systems. Ethernet switch shall be powered by 24VDC.-F01.07, 16

UR4.5.1 [URS-PCS-HR-013] All wiring inside the machine must be separated into power, signal, and network channels.-F01.10, 18

UR4.5.2 [URS-PCS-HR-014] Electrical enclosures shall be washdown duty, NEMA 4X rated.-F01.08, 17

UR4.5.3 [URS-PCS-HR-015] All electrical components shall be UL listed.-F01.10, 18

UR4.5.4 [URS-PCS-HR-016] A lockable disconnect switch shall be provided on each main feed to the PCS Miscellaneous PLC Panel

enclosure. The disconnect switch shall be rated per NEC guidelines of supplied voltage and current ratings (minimum 600VAC /

30A /-F01.11, 18

UR4.5.5 [MCCPDC 3.2.2] Completed, assembled panel shall be UL certified.-F01.10, 18

UR4.5.6 [MCCPDC 3.2.2] Completed, assembled panel shall be UL listed for the appropriate electrical area classification.-F01.10, 18

UR4.5.7 [MCCPDC 7.2.3] The SI shall provide PCS Miscellaneous PLC Panel Heat Load Calculation & Electrical Loading Calcs.

These calculations shall be maintained through to the final validated state As-Builts.-F01.08, 17

UR4.6.1 [URS-PCS-HR-017] All indicator lights shall be suitable for operation on 24VDC. Lamps (LED preferred) and caps shall be

replaceable from the outside front of the panel. For lamp caps specified as colored in hardware design specifications, the lamp-

F01.12, 18

UR4.7.1 [URS-PCS-HR-018] All components of the system shall be specified with a mean-time between failures of more than 2

years.-F01.13, 19

UR4.8.1 [URS-PCS-HR-019] System shall have the ability to alert users with an audible alert… (see below)-F01.14, 19

UR4.9.1 [URS-PCS-HR-020] Communication between SCADA and plant PLC’s shall be via Ethernet protocol. All communication

cabling shall be CAT6/CAT6A and in compliance with ANSI/TIA/EIA-568-B standards.-F01.06, 15

UR4.9.1 [URS-PCS-HR-020] Communication between SCADA and plant PLC’s shall be via Ethernet protocol. All communication

cabling shall be CAT6/CAT6A and in compliance with ANSI/TIA/EIA-568-B standards.-F01.07, 16

UR4.9.2 [URS-PCS-HR-021] All switching and cabling shall be capable of gigabit data transfer, where applicable.-F01.02, 13

UR4.9.2 [URS-PCS-HR-021] All switching and cabling shall be capable of gigabit data transfer, where applicable.-F01.06, 15

UR4.9.2 [URS-PCS-HR-021] All switching and cabling shall be capable of gigabit data transfer, where applicable.-F01.07, 16

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to the PCS Miscellaneous

PLC configuration and shall be capable of being connected to the OIT’s.-F01.03, 14

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to the PCS Miscellaneous

PLC configuration and shall be capable of being connected to the OIT’s.-F01.05, 15

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to the PCS Miscellaneous

PLC configuration and shall be capable of being connected to the OIT’s.-F01.07, 16

ID code: 215115305 -FS (V1.2) Page 56 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

UR5.1.1 [URS-PCS-SR-001] A SI provided Engineering Workstation perform online and offline changes to the PCS Miscellaneous

PLC configuration and shall be capable of being connected to the OIT’s.-F21.01, 52

UR5.1.2 [URS-PCS-SR-002] Distinction shall be drawn between, process interlocks, and safety interlocks lock out conditions.-

F07.00, 36

UR5.1.3 [URS-PCS-SR-005] All software source code shall be commented by the SI to convey intent and function of the code.-

F21.02, 53

UR5.1.4 [URS-PCS-SR-006] Revision history needed from initiation of SFAT, all revisions shall be approved and tracked.-F22.00,

53

UR5.2.1 [URS-PCS-SR-007] The system shall be configured to host an operator interface application.-F02.01, 19

UR5.2.10 [URS-PCS-SR-016] Alarm presentation shall be visual and audible.-F07.00, 36

UR5.2.11 [URS-PCS-SR-017] Alarms shall be displayed at the OIT as they occur. An alarm summary shall be available as a

navigable screen at the OIT.-F07.00, 36

UR5.2.12 [URS-PCS-SR-018] Each alarm should have its own description that is traceable for troubleshooting by a line operator or

maintenance person.-F07.00, 36

UR5.2.13 [URS-PCS-SR-019] Alarm acknowledgement and silencing of audible alarms shall be done from the OIT.-F07.00, 37

UR5.2.14 [URS-PCS-SR-020] Alarms shall be in one of the following categories- Unacknowledged (active or inactive),

Acknowledged (active), and Acknowledged (cleared).-F07.03, 37

UR5.2.15 [URS-PCS-SR-021] The system must be compatible with Windows 10 on laptop/desktop clients and/or Windows Terminal

Services.-F23.01, 53

UR5.2.16 [URS-PCS-SR-022] The system must detect and inform the operator of failures or errors in hardware and non-responsive

equipment.-F07.00, 37

UR5.2.17 [USR-PCS-SR-023] The PLC revision will be addressed to a PLC register, and hard coded OIT revision shall be accessible

via a main menu selection to users with Administrator or Engineer security level privileges.-F05.06, 24

UR5.2.18 [URS-PCS-SR-024] All soft key buttons shall be of sufficient size to allow finger touch of the object to activate it and have

adequate space between objects to ensure the correct object is being selected. Soft key button sizing and locations shal-F05.00, 22

UR5.2.19 [URS-PCS-SR-025] Real-time multi-pen trends for all analog and defined discrete signals. Also, PID loop controller

screens to include trending for PV, SP and CV as applicable.-F05.01, 23

UR5.2.2 [URS-PCS-SR-008] Control and privilege access shall be assigned to system users based on the following operator access

levels- Default User, Operator, Supervisor, Maintenance, Administrator.-F10.00, 40

UR5.2.20 [URS-PCS-SR-026] The following colors shall be utilized when indicating states of dynamic objects…(see below)-F05.02,

23

UR5.2.21 [URS-PCS-SR-027] The capability to generate an electronic or hard copy of any active display must be available via the

Print Screen function.-F05.03, 24

UR5.2.22 [URS-PCS-SR-028] Alarms shall be stored / available to view on an alarm history screen.-F07.00, 37

UR5.2.23 [URS-PCS-SR-029] The system shall provide an “Overview” screen on all physical OITs. The overview screen will display

“view-only” data for all critical parameters, values and information across the system. Details of the required overview informat-

F05.04, 24

UR5.2.3 [URS-PCS-SR-009] Logins, logouts, and login attempts must be recorded in the Audit Trail.-F12.00, 46

UR5.2.4 [URS-PCS-SR-010] The user identification must consist of two parts, username and password.-F10.05, 42

UR5.2.5 [URS-PCS-SR-011] System must be capable of utilizing active directory. It must be possible to configure the required

password strength of the user’s password with items such as # of capital letters, # of special characters, and length of the passwo-

F10.05, 43

UR5.2.6 [URS-PCS-SR-012] The system must have an automatic logout function that after a certain period of inactivity the user is

logged out to Default User.-F10.00, 40

UR5.2.7 [URS-PCS-SR-013] Interlock shall have associated alarms.-F07.00, 36

UR5.2.8 [URS-PCS-SR-014] Bypassed interlock conditions shall be clearly indicated at the OIT.-F07.00, 36

UR5.2.9 [URS-PCS-SR-015] The system shall provide display of analog signal status, numerical values, engineering units, and

alarming.-F05.00, 22

UR5.2.9 [URS-PCS-SR-015] The system shall provide display of analog signal status, numerical values, engineering units, and

alarming.-F07.00, 36

UR5.3.1 [URS-PCS-SR-030] The control system programming shall use Control Modules and standard programming per ISA

S88/S95 as applicable.-F02.01, 19

UR5.3.2 [URS-PCS-SR-031] Operations shall contain steps (series of actions) and transitions (conditions required for sequence to

progress) to perform required process sequences.-F02.01, 20

UR5.3.3 [URS-PCS-SR-032] All inputs shall provide state and simulation features. This shall be captured on a separate maintenance

screen, accessible by Admin and Maintenance personnel.-F02.03, 21

ID code: 215115305 -FS (V1.2) Page 57 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott

Project: Mark Cuban Cost Plus Drug Company, PBC –

MCCPDC - SCADA and PCS MISC. PLC System

Functional Specification for the MCCPDC - SCADA and PCS MISC. PLC System

UR5.3.3 [URS-PCS-SR-032] All inputs shall provide state and simulation features. This shall be captured on a separate maintenance

screen, accessible by Admin and Maintenance personnel.-F05.05, 24

UR5.3.4 [URS-PCS-SR-033] Alarms shall be classified into three priority categories unless alternative is approved by MCCPDC.

Level 1, Level 2, and Level 3 as described below.-F07.04, 38

UR5.3.5 [URS-PCS-SR-034] Alarm functionality is to include the ability to change alarm limit values via user input from the OIT

display. This functionality shall be secured level access for level 1 and level 2 alarms only. Changes shall only be capable fro-

F07.04, 38

UR5.4.1 [URS-PCS-SR-035] The system shall provide for an interface for the collection and archival of continuous process data,

alarms, alarm acknowledgement, events, parameters, and ancillary data.-F02.01, 20

UR5.4.2 [URS-PCS-SR-036] All manual interactions (parameter changes, device mode changes, etc.) shall be sent to a database for

event logging, including user name, action and timestamp.-F12.00, 46

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).-F01.02, 13

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).-F01.05, 15

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).-F01.06, 15

UR5.4.3 [URS-PCS-SR-037] All data communication shall be via Ethernet (protocol).-F01.07, 16

UR5.4.4 [URS-PCS-SR-038] The system must provide tools to automatically adjust for daylight and standard time changes without

loss of data or operation.-F02.01, 20

UR5.4.5 [URS-PCS-SR-039] The system shall monitor and alarm the status of all dependent external interfaces.-F07.05, 39

UR5.4.6 [URS-PCS-SR-040] The system shall communicate via OPC standard communication protocol for data transfer outside of

the PLC control system layer.-F17.00, 50

UR5.4.7 [URS-PCS-SR-041] The PLC system shall communicate with a plant historian (collect and transfer data).-F02.01, 20

UR5.4.7 [URS-PCS-SR-041] The PLC system shall communicate with a plant historian (collect and transfer data).-F11.00, 45

UR5.4.8 [URS-PCS-SR-042] The control system shall have a historian heartbeat alarm to monitor the health of control system

communication with the process historian. In absence of an active connection, this heartbeat alarm will be triggered, however the

PLC-F07.06, 39

UR5.4.9 [URS-PCS-SR-043] A secured level access manual override shall be required / available to start a new batch without active

heartbeat connection to the plant historian.-F02.04, 21

UR6.1.1 [MCCPDC 3.3.3] - The project shall utilize the GAMP methodology when developing the system and documentation.-

F17.00, 51

UR6.1.2 System is documented via entries found in URS Table 2- List of Documents.-F17.00, 51

ID code: 215115305 -FS (V1.2) Page 58 of 58

© 2022 Rockwell Automation, Inc. All Rights Reserved / Author: Buol, Scott